## HP Calculations
Tevaporation
|  | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44 | at 70 celcius |  |  |  | at 50 celcius
| H1 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 |  |  |  | P2=P3 | 2.1168 | MPa |  | P2=P3 | 1.3179 | MPa
| H2 | 386.55 | 389.02 | 391.46 | 393.87 | 396.25 | 398.6 | 400.92 | 403.2 | 405.43 | 407.61 | 409.75 | 411.82 | 413.84 | 415.78 | 417.65 | 419.43 | 421.11 | H4 | 428.65 | kj/kg |  | H4 | 423.44 | kj/kg
| S2=S1 | 1.7413 | 1.7379 | 1.7348 | 1.732 | 1.7294 | 1.7271 | 1.725 | 1.723 | 1.7212 | 1.7196 | 1.718 | 1.7166 | 1.7152 | 1.7138 | 1.7124 | 1.7111 | 1.7096 | H5 | 304.28 |  |  | H5 | 271.62
| H3 at 70 | 444.5933 | 443.3907 | 442.2941 | 441.3037 | 440.3884 | 439.5859 | 438.8532 | 438.1554 | 437.5274 | 436.9691 | 436.4109 | 435.9224 | 435.4339 | 434.9455 | 434.457 | 434.0034 | 433.4801 | S4 | 1.6956 | kj/kg.K |  | S4 | 1.7072 | kj/kg.K
| H3 at 50 | 434.5756 | 433.4406 | 432.4058 | 431.4844 | 430.6294 | 429.873 | 429.1824 | 428.5246 | 427.9372 | 427.4163 | 426.8953 | 426.4395 | 425.9837 | 425.5278 | 425.072 | 424.6487 | 424.1603 | S5 | 1.3332 |  |  | S5 | 1.2375
|  | pressure | 2 | [6 empty] | Pressure | 2.2 | [6 empty] | pressure | 2.1168 |  |  | pressure | 1.2 |  |  | Pressure | 1.4
|  | Temp | H | S | [5 empty] | Temp | H | S | [5 empty] | Temp3 | H3 |  |  | Temp | H | S |  | Temp | H | S
|  | 67.49 | 428.52 | 1.6983 | [5 empty] | 71.74 | 429.08 | 1.6948 | [9 empty] | 46.32 | 422.22 | 1.7092 |  | 52.43 | 424.5 | 1.7068
|  | 70 | 432.22 | 1.7091 | [17 empty] | 50 | 426.51 | 1.7226 |  | 60 | 433.69 | 1.7347
|  | 80 | 445.86 | 1.7483 | [5 empty] | 80 | 441.49 | 1.7303 | [9 empty] | 60 | 437.83 | 1.7571 |  | 70 | 445.31 | 1.7691
|  | 90 | 458.49 | 1.7835 | [5 empty] | 90 | 454.98 | 1.768 | [9 empty] | 70 |  |  |  | 80
|  | 100 | [7 empty] | 100 | 467.61 | 1.8023 | [9 empty] | 80 |  |  |  | 90
Linear interpolatation
H3 calculator
| at S70,p=2 | 443.4243 | 442.2412 | 441.1626 | 440.1883 | 439.2836 | 438.4833 | 437.7526 | 437.0566 | 436.4303 | 435.8736 | 435.3168 | 434.8297 | 434.3426 | 433.8554 | 433.3683 | 432.9159 | 432.394
| at S50, p = 1.2 | 432.6458 | 431.5302 | 430.513 | 429.5943 | 428.7412 | 427.9865 | 427.2975 | 426.6412 | 426.0618 | 425.5496 | 425.0373 | 424.5891 | 424.1409 | 423.6927 | 423.2445 | 422.8283 | 422.3481
Results
W (kj/kg) | H3-H2 | 58.0433 | 54.3707 | 50.8341 | 47.4337 | 44.1384 | 40.9859 | 37.9332 | 34.9554 | 32.0974 | 29.3591 | 26.6609 | 24.1024 | 21.5939 | 19.1655 | 16.807 | 14.5734 | 12.3701
Q(kj/kg) | H3-H5 | 140.3133 | 139.1107 | 138.0141 | 137.0237 | 136.1084 | 135.3059 | 134.5732 | 133.8754 | 133.2474 | 132.6891 | 132.1309 | 131.6424 | 131.1539 | 130.6655 | 130.177 | 129.7234 | 129.2001
COP at 70 | Q/W | 2.4174 | 2.5586 | 2.715 | 2.8887 | 3.0837 | 3.3013 | 3.5476 | 3.8299 | 4.1513 | 4.5195 | 4.956 | 5.4618 | 6.0736 | 6.8178 | 7.7454 | 8.9014 | 10.4446
COP at 50 |  | 3.3931 | 3.6429 | 3.9268 | 4.2501 | 4.6251 | 5.0604 | 5.575 | 6.1957 | 6.9452 | 7.866 | 9.0564 | 10.5899 | 12.7115 | 15.7889 | 20.6753 | 29.3231 | 50.008
cycle efficiency | COP(Tcon-Teva)/Teva | 0.85943 | 0.85567 | 0.8525 | 0.84979 | 0.84782 | 0.84602 | 0.84483 | 0.84458 | 0.84439 | 0.84404 | 0.8453 | 0.84551 | 0.84706 | 0.84901 | 0.85183 | 0.85276 | 0.85625
| at 50 | 0.93825 | 0.93499 | 0.93227 | 0.92968 | 0.92795 | 0.9263 | 0.92531 | 0.92556 | 0.92554 | 0.92493 | 0.9268 | 0.9266 | 0.92861 | 0.93135 | 0.93629 | 0.93639 | 0.94608
m(kg/s) | 50000(kW)/(Q) | 356.3453 | 359.426 | 362.2817 | 364.9003 | 367.3543 | 369.533 | 371.545 | 373.4816 | 375.2419 | 376.8206 | 378.4127 | 379.8168 | 381.2314 | 382.6565 | 384.0924 | 385.4354 | 386.9967
W (kj/kg) | H3-H2 | 48.0256 | 44.4206 | 40.9458 | 37.6144 | 34.3794 | 31.273 | 28.2624 | 25.3246 | 22.5072 | 19.8063 | 17.1453 | 14.6195 | 12.1437 | 9.7478 | 7.422 | 5.2187 | 3.0503
Q(kj/kg) | H3-H5 | 162.9556 | 161.8206 | 160.7858 | 159.8644 | 159.0094 | 158.253 | 157.5624 | 156.9046 | 156.3172 | 155.7963 | 155.2753 | 154.8195 | 154.3637 | 153.9078 | 153.452 | 153.0287 | 152.5403
| at S70,p=2.2 | 445.4261 | 444.2095 | 443.1002 | 442.0983 | 441.1754 | 440.3714 | 439.6372 | 438.9381 | 438.3088 | 437.7495 | 437.1902 | 436.7008 | 436.2114 | 435.722 | 435.2326 | 434.7781 | 434.2537
| at S50, p = 1.4 | 435.9194 | 434.7709 | 433.7238 | 432.8006 | 431.9442 | 431.1866 | 430.4949 | 429.8361 | 429.2432 | 428.7162 | 428.1892 | 427.728 | 427.2669 | 426.8057 | 426.3446 | 425.9164 | 425.4223
| final at 70 | 444.5933 | 443.3907 | 442.2941 | 441.3037 | 440.3884 | 439.5859 | 438.8532 | 438.1554 | 437.5274 | 436.9691 | 436.4109 | 435.9224 | 435.4339 | 434.9455 | 434.457 | 434.0034 | 433.4801
| final at 50 | 434.5756 | 433.4406 | 432.4058 | 431.4844 | 430.6294 | 429.873 | 429.1824 | 428.5246 | 427.9372 | 427.4163 | 426.8953 | 426.4395 | 425.9837 | 425.5278 | 425.072 | 424.6487 | 424.1603

## p-H cycle table
1
2
3
4
5

## COPat50 vs. Teva
Teva |  | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
COP at 50
|  | 3.3931 | 3.6429 | 3.9268 | 4.2501 | 4.6251 | 5.0604 | 5.575 | 6.1957 | 6.9452 | 7.866 | 9.0564 | 10.5899 | 12.7115 | 15.7889 | 20.6753 | 29.3231 | 50.008
| -20 | 3.3931
| -16 | 3.6429
| -12 | 3.9268
| -8 | 4.2501 | [13 empty] | Linear model Poly5: f(x) = p1*x^5 + p2*x^4 + p3*x^3 + p4*x^2 + p5*x + p6 Coefficients (with 95% confidence bounds): p1 = 3.461e-08 (2.389e-08, 4.533e-08) p2 = 1.29e-06 (1.131e-06, 1.449e-06) p3 = 4.353e-05 (3.721e-05, 4.984e-05) p4 = 0.002387 (0.002319, 0.002455) p5 = 0.1186 (0.1178, 0.1195) p6 = 5.063 (5.057, 5.068) Goodness of fit: SSE: 8.541e-05 R-square: 1 Adjusted R-square: 1 RMSE: 0.003773
| -4 | 4.6251
| 0 | 5.0604
| 4 | 5.575
| 8 | 6.1957
| 12 | 6.9452
| 16 | 7.866
| 20 | 9.0564
| 24 | 10.5899
| 28 | 12.7115
| 32 | 15.7889
| 36 | 20.6753
| 40 | 29.3231
| 44 | 50.008

## COPat70 vs. Teva
Teva | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
COP
| 2.4174 | 2.5586 | 2.715 | 2.8887 | 3.0837 | 3.3013 | 3.5476 | 3.8299 | 4.1513 | 4.5195 | 4.956 | 5.4618 | 6.0736 | 6.8178 | 7.7454 | 8.9014 | 10.4446
5th order polynomial function
Linear model Poly5: f(x) = p1*x^5 + p2*x^4 + p3*x^3 + p4*x^2 + p5*x + p6 Coefficients (with 95% confidence bounds): p1 = 1.457e-08 (1.116e-08, 1.798e-08) p2 = -9.658e-08 (-3.086e-07, 1.154e-07) p3 = 6.609e-06 (3.71e-06, 9.508e-06) p4 = 0.00101 (0.000908, 0.001112) p5 = 0.05864 (0.05748, 0.05979) p6 = 3.295 (3.284, 3.306) Goodness of fit: SSE: 0.001116 R-square: 1 Adjusted R-square: 1 RMSE: 0.01007
| x | y
| -20 | 2.4174
| -16 | 2.5586
| -12 | 2.715
| -8 | 2.8887
| -4 | 3.0837
| 0 | 3.3013
| 4 | 3.5476
| 8 | 3.8299
| 12 | 4.1513
| 16 | 4.5195
| 20 | 4.956
| 24 | 5.4618
| 28 | 6.0736
| 32 | 6.8178
| 36 | 7.7454
| 40 | 8.9014
| 44 | 10.4446

## P2H Models
Modelling Considerations of P2H
Model | Modelling Approach | Dynamic Behaviour | Modelling Scale | COP
A | Regression | Linear | HP | Constant
B | Regression | Non-linear | HP | Variable
C | Regression | Non-linear | HP with auxiliary boiler | Constant
Tcondenser | a1 | a2 | a3 | a4 | a5 | a6
50 | 3.461e-08 | 1.29e-06 | 4.353e-05 | 0.002387 | 0.1186 | 5.063
70 | 1.457e-08 | -9.658e-08 | 6.609e-06 | 0.00101 | 0.05864 | 3.295

## Boiler
Q | m*c*∆T(40-Twaste)
η | efficiency | 0.99
W | Q/η
m | mass/massflow R134a |  | kg/s
c | specific heat capacity |  | kJ/(kg.K) | at 40 celcius quality=0.5
Tevaporation
| -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
H1 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28
H2 | 386.55 | 389.02 | 391.46 | 393.87 | 396.25 | 398.6 | 400.92 | 403.2 | 405.43 | 407.61 | 409.75 | 411.82 | 413.84 | 415.78 | 417.65 | 419.43 | 421.11
H2-H1 | 82.27 | 84.74 | 87.18 | 89.59 | 91.97 | 94.32 | 96.64 | 98.92 | 101.15 | 103.33 | 105.47 | 107.54 | 109.56 | 111.5 | 113.37 | 115.15 | 116.83
|  | Tamb | Q
|  | -20 | 82.27
|  | -16 | 84.74
|  | -12 | 87.18
|  | -8 | 89.59
|  | -4 | 91.97
|  | 0 | 94.32
|  | 4 | 96.64
|  | 8 | 98.92
|  | 12 | 101.15
|  | 16 | 103.33
|  | 20 | 105.47
|  | 24 | 107.54
|  | 28 | 109.56
|  | 32 | 111.5
|  | 36 | 113.37
|  | 40 | 115.15
|  | 44 | 116.83

## Tamb
Weather archive in Hoek Van Holland weather station number :06330 https://rp5.ru/Weather_archive_in_Hoek_Van_Holland
Ambient Air temperature at 2m
[14 empty] | TReference | Tmin | m0 [m3/s] | mmax [m3/s]
[13 empty] | Industrial PtG | 25 | 5 | 0.0031372 | 0.0038502
Hour\Day | 2019-02-07 |  |  | 2019-03-23 |  |  | 2019-05-07 |  |  | 2019-06-23 |  |  | District Heating PtH | 25 | 5 | 3 | 4
| Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s)
0:00 | 6.8 | 0.003786 | 3.91 | 8.6 | 0.0037219 | 3.82 | 5.3 | 0.0038395 | 3.985 | 16.6 | 0.0034367 | 3.42 | 0.98333 | 0.782 |  | 0.96667 | 0.764 | 0.99722 | 0.797 | 0.89259 | 0.684 | 3.91
1:00 | 6.9 | 0.0037825 | 3.905 | 8.8 | 0.0037147 | 3.81 | 5.5 | 0.0038324 | 3.975 | 17 | 0.0034224 | 3.4 | 0.98241 | 0.781 |  | 0.96481 | 0.762 | 0.99537 | 0.795 | 0.88889 | 0.68 | 3.905
2:00 | 7.3 | 0.0037682 | 3.885 | 8.8 | 0.0037147 | 3.81 | 5 | 0.0038502 | 4 | 16.6 | 0.0034367 | 3.42 | 0.9787 | 0.777 |  | 0.96481 | 0.762 | 1 | 0.8 | 0.89259 | 0.684 | 3.885
3:00 | 7.8 | 0.0037504 | 3.86 | 8.7 | 0.0037183 | 3.815 | 5.1 | 0.0038466 | 3.995 | 16 | 0.0034581 | 3.45 | 0.97407 | 0.772 |  | 0.96574 | 0.763 | 0.99907 | 0.799 | 0.89815 | 0.69 | 3.86
4:00 | 8.1 | 0.0037397 | 3.845 | 8.7 | 0.0037183 | 3.815 | 4.9 | 0.0038538 | 4.005 | 15.5 | 0.0034759 | 3.475 | 0.9713 | 0.769 |  | 0.96574 | 0.763 | 1.0009 | 0.801 | 0.90278 | 0.695 | 3.845
5:00 | 8.8 | 0.0037147 | 3.81 | 9 | 0.0037076 | 3.8 | 4.9 | 0.0038538 | 4.005 | 15 | 0.0034937 | 3.5 | 0.96481 | 0.762 |  | 0.96296 | 0.76 | 1.0009 | 0.801 | 0.90741 | 0.7 | 3.81
6:00 | 9 | 0.0037076 | 3.8 | 9.2 | 0.0037005 | 3.79 | 5.3 | 0.0038395 | 3.985 | 14.9 | 0.0034973 | 3.505 | 0.96296 | 0.76 |  | 0.96111 | 0.758 | 0.99722 | 0.797 | 0.90833 | 0.701 | 3.8
7:00 | 7.4 | 0.0037646 | 3.88 | 9.1 | 0.003704 | 3.795 | 6.1 | 0.003811 | 3.945 | 16.3 | 0.0034474 | 3.435 | 0.97778 | 0.776 |  | 0.96204 | 0.759 | 0.98981 | 0.789 | 0.89537 | 0.687 | 3.88
8:00 | 6.8 | 0.003786 | 3.91 | 9.3 | 0.0036969 | 3.785 | 8 | 0.0037433 | 3.85 | 17.8 | 0.0033939 | 3.36 | 0.98333 | 0.782 |  | 0.96019 | 0.757 | 0.97222 | 0.77 | 0.88148 | 0.672 | 3.91
9:00 | 6.7 | 0.0037896 | 3.915 | 9.4 | 0.0036933 | 3.78 | 9.3 | 0.0036969 | 3.785 | 19.9 | 0.003319 | 3.255 | 0.98426 | 0.783 |  | 0.95926 | 0.756 | 0.96019 | 0.757 | 0.86204 | 0.651 | 3.915
10:00 | 7.1 | 0.0037753 | 3.895 | 9.3 | 0.0036969 | 3.785 | 11.5 | 0.0036185 | 3.675 | 22.2 | 0.003237 | 3.14 | 0.98056 | 0.779 |  | 0.96019 | 0.757 | 0.93981 | 0.735 | 0.84074 | 0.628 | 3.895
11:00 | 7.8 | 0.0037504 | 3.86 | 9.4 | 0.0036933 | 3.78 | 10.3 | 0.0036613 | 3.735 | 24.4 | 0.0031586 | 3.03 | 0.97407 | 0.772 |  | 0.95926 | 0.756 | 0.95093 | 0.747 | 0.82037 | 0.606 | 3.86
12:00 | 8.1 | 0.0037397 | 3.845 | 9.1 | 0.003704 | 3.795 | 12.5 | 0.0035828 | 3.625 | 23.3 | 0.0031978 | 3.085 | 0.9713 | 0.769 |  | 0.96204 | 0.759 | 0.93056 | 0.725 | 0.83056 | 0.617 | 3.845
13:00 | 8.6 | 0.0037219 | 3.82 | 9.7 | 0.0036826 | 3.765 | 13.5 | 0.0035472 | 3.575 | 22.8 | 0.0032156 | 3.11 | 0.96667 | 0.764 |  | 0.95648 | 0.753 | 0.9213 | 0.715 | 0.83519 | 0.622 | 3.82
14:00 | 8.6 | 0.0037219 | 3.82 | 9.9 | 0.0036755 | 3.755 | 12.7 | 0.0035757 | 3.615 | 24.2 | 0.0031657 | 3.04 | 0.96667 | 0.764 |  | 0.95463 | 0.751 | 0.9287 | 0.723 | 0.82222 | 0.608 | 3.82
15:00 | 8.2 | 0.0037361 | 3.84 | 9.9 | 0.0036755 | 3.755 | 14 | 0.0035294 | 3.55 | 24 | 0.0031729 | 3.05 | 0.97037 | 0.768 |  | 0.95463 | 0.751 | 0.91667 | 0.71 | 0.82407 | 0.61 | 3.84
16:00 | 7.8 | 0.0037504 | 3.86 | 9.4 | 0.0036933 | 3.78 | 14.6 | 0.003508 | 3.52 | 28.2 | 0.0031372 | 3 | 0.97407 | 0.772 |  | 0.95926 | 0.756 | 0.91111 | 0.704 | 0.81481 | 0.6 | 3.86
17:00 | 7.2 | 0.0037718 | 3.89 | 9.2 | 0.0037005 | 3.79 | 14.4 | 0.0035151 | 3.53 | 28.7 | 0.0031372 | 3 | 0.97963 | 0.778 |  | 0.96111 | 0.758 | 0.91296 | 0.706 | 0.81481 | 0.6 | 3.89
18:00 | 7 | 0.0037789 | 3.9 | 8.2 | 0.0037361 | 3.84 | 14.6 | 0.003508 | 3.52 | 28.6 | 0.0031372 | 3 | 0.98148 | 0.78 |  | 0.97037 | 0.768 | 0.91111 | 0.704 | 0.81481 | 0.6 | 3.9
19:00 | 6.9 | 0.0037825 | 3.905 | 7.2 | 0.0037718 | 3.89 | 14.1 | 0.0035258 | 3.545 | 27.8 | 0.0031372 | 3 | 0.98241 | 0.781 |  | 0.97963 | 0.778 | 0.91574 | 0.709 | 0.81481 | 0.6 | 3.905
20:00 | 6.7 | 0.0037896 | 3.915 | 6.9 | 0.0037825 | 3.905 | 13.5 | 0.0035472 | 3.575 | 27.2 | 0.0031372 | 3 | 0.98426 | 0.783 |  | 0.98241 | 0.781 | 0.9213 | 0.715 | 0.81481 | 0.6 | 3.915
21:00 | 6.5 | 0.0037967 | 3.925 | 6.5 | 0.0037967 | 3.925 | 12.2 | 0.0035935 | 3.64 | 26.4 | 0.0031372 | 3 | 0.98611 | 0.785 |  | 0.98611 | 0.785 | 0.93333 | 0.728 | 0.81481 | 0.6 | 3.925
22:00 | 6.4 | 0.0038003 | 3.93 | 5.8 | 0.0038217 | 3.96 | 11.2 | 0.0036292 | 3.69 | 24.9 | 0.0031408 | 3.005 | 0.98704 | 0.786 |  | 0.99259 | 0.792 | 0.94259 | 0.738 | 0.81574 | 0.601 | 3.93
23:00 | 6.3 | 0.0038039 | 3.935 | 5.1 | 0.0038466 | 3.995 | 11.1 | 0.0036327 | 3.695 | 24.2 | 0.0031657 | 3.04 | 0.98796 | 0.787 |  | 0.99907 | 0.799 | 0.94352 | 0.739 | 0.82222 | 0.608 | 3.935
Average | 7.45 | 0.0037629 |  | 8.55 | 0.0037236 |  | 9.9833 | 0.0036725 | 3.7508 | 21.7708 | 0.0032774 | 3.1967 | 0.97731 | 0 |  | 0.96713 | 0 | 0.95386 | 0.75017 | 0.85123 | 0.63933 | 3.82
Hour\Day | 2019-08-07 |  |  | 2019-09-23 |  |  | 2019-11-07 |  |  | 2019-12-23 | [11 empty] | 3.81
| Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | [9 empty] | 3.81
0:00 | 18.6 | 0.0033654 | 3.32 | 16.1 | 0.0034545 | 3.445 | 7.1 | 0.0037753 | 3.895 | 8.6 | 0.0037219 | 3.82 | 0.87407 | 0.664 |  | 0.89722 | 0.689 | 0.98056 | 0.779 | 0.96667 | 0.764 | 3.815
1:00 | 18.7 | 0.0033618 | 3.315 | 16 | 0.0034581 | 3.45 | 6.8 | 0.003786 | 3.91 | 8.7 | 0.0037183 | 3.815 | 0.87315 | 0.663 |  | 0.89815 | 0.69 | 0.98333 | 0.782 | 0.96574 | 0.763 | 3.815
2:00 | 18.4 | 0.0033725 | 3.33 | 15.9 | 0.0034616 | 3.455 | 6.1 | 0.003811 | 3.945 | 8.9 | 0.0037112 | 3.805 | 0.87593 | 0.666 |  | 0.89907 | 0.691 | 0.98981 | 0.789 | 0.96389 | 0.761 | 3.8
3:00 | 18.5 | 0.0033689 | 3.325 | 15.9 | 0.0034616 | 3.455 | 6.2 | 0.0038074 | 3.94 | 8.7 | 0.0037183 | 3.815 | 0.875 | 0.665 |  | 0.89907 | 0.691 | 0.98889 | 0.788 | 0.96574 | 0.763 | 3.79
4:00 | 18.3 | 0.0033761 | 3.335 | 15.8 | 0.0034652 | 3.46 | 6.1 | 0.003811 | 3.945 | 8.4 | 0.003729 | 3.83 | 0.87685 | 0.667 |  | 0.9 | 0.692 | 0.98981 | 0.789 | 0.96852 | 0.766 | 3.795
5:00 | 18 | 0.0033868 | 3.35 | 15.7 | 0.0034687 | 3.465 | 7.2 | 0.0037718 | 3.89 | 8.2 | 0.0037361 | 3.84 | 0.87963 | 0.67 |  | 0.90093 | 0.693 | 0.97963 | 0.778 | 0.97037 | 0.768 | 3.785
6:00 | 18 | 0.0033868 | 3.35 | 15.8 | 0.0034652 | 3.46 | 7.6 | 0.0037575 | 3.87 | 8.4 | 0.003729 | 3.83 | 0.87963 | 0.67 |  | 0.9 | 0.692 | 0.97593 | 0.774 | 0.96852 | 0.766 | 3.78
7:00 | 17.2 | 0.0034153 | 3.39 | 15.7 | 0.0034687 | 3.465 | 8 | 0.0037433 | 3.85 | 7.5 | 0.0037611 | 3.875 | 0.88704 | 0.678 |  | 0.90093 | 0.693 | 0.97222 | 0.77 | 0.97685 | 0.775 | 3.785
8:00 | 18.1 | 0.0033832 | 3.345 | 15.7 | 0.0034687 | 3.465 | 7.7 | 0.0037539 | 3.865 | 7.4 | 0.0037646 | 3.88 | 0.8787 | 0.669 |  | 0.90093 | 0.693 | 0.975 | 0.773 | 0.97778 | 0.776 | 3.78
9:00 | 18.7 | 0.0033618 | 3.315 | 15.7 | 0.0034687 | 3.465 | 8.3 | 0.0037326 | 3.835 | 8.3 | 0.0037326 | 3.835 | 0.87315 | 0.663 |  | 0.90093 | 0.693 | 0.96944 | 0.767 | 0.96944 | 0.767 | 3.795
10:00 | 19.2 | 0.003344 | 3.29 | 16 | 0.0034581 | 3.45 | 8.7 | 0.0037183 | 3.815 | 8.1 | 0.0037397 | 3.845 | 0.86852 | 0.658 |  | 0.89815 | 0.69 | 0.96574 | 0.763 | 0.9713 | 0.769 | 3.765
11:00 | 20.1 | 0.0033119 | 3.245 | 16.1 | 0.0034545 | 3.445 | 8.7 | 0.0037183 | 3.815 | 8.3 | 0.0037326 | 3.835 | 0.86019 | 0.649 |  | 0.89722 | 0.689 | 0.96574 | 0.763 | 0.96944 | 0.767 | 3.755
12:00 | 20.4 | 0.0033012 | 3.23 | 17.7 | 0.0033974 | 3.365 | 8.7 | 0.0037183 | 3.815 | 8.5 | 0.0037254 | 3.825 | 0.85741 | 0.646 |  | 0.88241 | 0.673 | 0.96574 | 0.763 | 0.96759 | 0.765 | 3.755
13:00 | 17.7 | 0.0033974 | 3.365 | 16.8 | 0.0034295 | 3.41 | 8.3 | 0.0037326 | 3.835 | 8.8 | 0.0037147 | 3.81 | 0.88241 | 0.673 |  | 0.89074 | 0.682 | 0.96944 | 0.767 | 0.96481 | 0.762 | 3.78
14:00 | 20.1 | 0.0033119 | 3.245 | 17.9 | 0.0033903 | 3.355 | 8.4 | 0.003729 | 3.83 | 8.8 | 0.0037147 | 3.81 | 0.86019 | 0.649 |  | 0.88056 | 0.671 | 0.96852 | 0.766 | 0.96481 | 0.762 | 3.79
15:00 | 21.7 | 0.0032548 | 3.165 | 19.1 | 0.0033475 | 3.295 | 8.1 | 0.0037397 | 3.845 | 8.9 | 0.0037112 | 3.805 | 0.84537 | 0.633 |  | 0.86944 | 0.659 | 0.9713 | 0.769 | 0.96389 | 0.761 | 3.84
16:00 | 21.8 | 0.0032513 | 3.16 | 19.1 | 0.0033475 | 3.295 | 8.3 | 0.0037326 | 3.835 | 8.4 | 0.003729 | 3.83 | 0.84444 | 0.632 |  | 0.86944 | 0.659 | 0.96944 | 0.767 | 0.96852 | 0.766 | 3.89
17:00 | 21.9 | 0.0032477 | 3.155 | 18.4 | 0.0033725 | 3.33 | 8.8 | 0.0037147 | 3.81 | 8.4 | 0.003729 | 3.83 | 0.84352 | 0.631 |  | 0.87593 | 0.666 | 0.96481 | 0.762 | 0.96852 | 0.766 | 3.905
18:00 | 21.5 | 0.003262 | 3.175 | 18.6 | 0.0033654 | 3.32 | 9.2 | 0.0037005 | 3.79 | 8.2 | 0.0037361 | 3.84 | 0.84722 | 0.635 |  | 0.87407 | 0.664 | 0.96111 | 0.758 | 0.97037 | 0.768 | 3.925
19:00 | 20.8 | 0.0032869 | 3.21 | 17.5 | 0.0034046 | 3.375 | 7.9 | 0.0037468 | 3.855 | 8.1 | 0.0037397 | 3.845 | 0.8537 | 0.642 |  | 0.88426 | 0.675 | 0.97315 | 0.771 | 0.9713 | 0.769 | 3.96
20:00 | 19.8 | 0.0033226 | 3.26 | 15.6 | 0.0034723 | 3.47 | 7.4 | 0.0037646 | 3.88 | 8.5 | 0.0037254 | 3.825 | 0.86296 | 0.652 |  | 0.90185 | 0.694 | 0.97778 | 0.776 | 0.96759 | 0.765 | 3.995
21:00 | 19 | 0.0033511 | 3.3 | 15 | 0.0034937 | 3.5 | 7.2 | 0.0037718 | 3.89 | 9 | 0.0037076 | 3.8 | 0.87037 | 0.66 |  | 0.90741 | 0.7 | 0.97963 | 0.778 | 0.96296 | 0.76 | 3.985
22:00 | 19 | 0.0033511 | 3.3 | 13.8 | 0.0035365 | 3.56 | 6.9 | 0.0037825 | 3.905 | 8.6 | 0.0037219 | 3.82 | 0.87037 | 0.66 |  | 0.91852 | 0.712 | 0.98241 | 0.781 | 0.96667 | 0.764 | 3.975
23:00 | 18.9 | 0.0033547 | 3.305 | 15.8 | 0.0034652 | 3.46 | 6.5 | 0.0037967 | 3.925 | 8 | 0.0037433 | 3.85 | 0.8713 | 0.661 |  | 0.9 | 0.692 | 0.98611 | 0.785 | 0.97222 | 0.77 | 4
Average | 19.35 | 0.0033386 | 3.2825 | 16.4875 | 0.0034407 | 3.4256 | 7.675 | 0.0037548 | 3.8662 | 8.4042 | 0.0037288 | 3.8298 | 0.86713 | 0.6565 |  | 0.89363 | 0.68512 | 0.97523 | 0.77325 | 0.96848 | 0.76596 | 3.995
4.005
4.005
3.985
3.945
3.85
3.785
3.675
3.735
3.625
3.575
3.615
3.55
3.52
3.53
3.52
3.545
3.575
3.64
|  | slope hydrogen | 3.565e-05 | [18 empty] | 3.69
|  |  | 3.565e-05 | [18 empty] | 3.695
|  |  | 3.565e-05 | [18 empty] | 3.42
|  |  | 3.565e-05 | [18 empty] | 3.4
|  |  | 3.565e-05 | [18 empty] | 3.42
|  |  | 3.565e-05 | [18 empty] | 3.45
|  |  | 3.565e-05 | [18 empty] | 3.475
|  |  | 3.565e-05 | [18 empty] | 3.5
|  |  | 3.565e-05 | [18 empty] | 3.505
|  |  | 3.565e-05 | [18 empty] | 3.435
|  |  | 3.565e-05 | [18 empty] | 3.36
|  |  | 3.565e-05 | [18 empty] | 3.255
|  |  | 3.565e-05 | [18 empty] | 3.14
|  |  | 3.565e-05 | [18 empty] | 3.03
|  |  | 3.565e-05 | [18 empty] | 3.085
|  |  | 3.565e-05 | [18 empty] | 3.11
|  |  | 3.565e-05 | [18 empty] | 3.04
|  |  | 3.565e-05 | [18 empty] | 3.05
|  |  | 3.565e-05 | [18 empty] | 3
|  |  | 3.565e-05 | [18 empty] | 3
|  |  | 3.565e-05 | [18 empty] | 3
|  |  | 3.565e-05 | [18 empty] | 3
|  |  | 3.565e-05 | [18 empty] | 3
|  |  | 3.565e-05 | [18 empty] | 3
|  |  | 3.565e-05 | [18 empty] | 3.005
|  |  | 3.565e-05 | [18 empty] | 3.04
|  |  | 3.565e-05 | [18 empty] | 3.32
|  |  | 3.565e-05 | [18 empty] | 3.315
|  |  | 3.565e-05 | [18 empty] | 3.33
3.325
3.335
3.35
3.35
3.39
3.345
3.315
3.29
3.245
3.23
3.365
3.245
3.165
3.16
3.155
3.175
3.21
3.26
3.3
3.3
3.305
3.445
3.45
3.455
3.455
3.46
3.465
3.46
3.465
3.465
3.465
3.45
3.445
3.365
3.41
3.355
3.295
3.295
3.33
3.32
3.375
3.47
3.5
3.56
3.46
3.895
3.91
3.945
3.94
3.945
3.89
3.87
3.85
3.865
3.835
3.815
3.815
3.815
3.835
3.83
3.845
3.835
3.81
3.79
3.855
3.88
3.89
3.905
3.925
3.82
3.815
3.805
3.815
3.83
3.84
3.83
3.875
3.88
3.835
3.845
3.835
3.825
3.81
3.81
3.805
3.83
3.83
3.84
3.845
3.825
3.8
3.82
3.85

## normalized demand
| Date | Time | Hydrogen | Heat |  |  | Tamb | Tamb_avg
0 |  | 0:00 | 0.98333 | 0.964 | 0.003786 | 3.856 | 6.8 | 7.45
1 |  | 1:00 | 0.98241 | 0.962 | 0.0037825 | 4.81 | 6.9 | 7.45
2 |  | 2:00 | 0.9787 | 0.954 | 0.0037682 | 4.77 | 7.3 | 7.45
3 |  | 3:00 | 0.97407 | 0.944 | 0.0037504 | 4.72 | 7.8 | 7.45
4 |  | 4:00 | 0.9713 | 0.938 | 0.0037397 | 4.69 | 8.1 | 7.45
5 |  | 5:00 | 0.96481 | 0.924 | 0.0037147 | 4.62 | 8.8 | 7.45
6 |  | 6:00 | 0.96296 | 0.92 | 0.0037076 | 4.6 | 9 | 7.45
7 |  | 7:00 | 0.97778 | 0.952 | 0.0037646 | 4.76 | 7.4 | 7.45
8 |  | 8:00 | 0.98333 | 0.964 | 0.003786 | 4.82 | 6.8 | 7.45
9 |  | 9:00 | 0.98426 | 0.966 | 0.0037896 | 4.83 | 6.7 | 7.45
10 |  | 10:00 | 0.98056 | 0.958 | 0.0037753 | 4.79 | 7.1 | 7.45
11 |  | 11:00 | 0.97407 | 0.944 | 0.0037504 | 4.72 | 7.8 | 7.45
12 |  | 12:00 | 0.9713 | 0.938 | 0.0037397 | 4.69 | 8.1 | 7.45
13 |  | 13:00 | 0.96667 | 0.928 | 0.0037219 | 4.64 | 8.6 | 7.45
14 |  | 14:00 | 0.96667 | 0.928 | 0.0037219 | 4.64 | 8.6 | 7.45
15 |  | 15:00 | 0.97037 | 0.936 | 0.0037361 | 4.68 | 8.2 | 7.45
16 |  | 16:00 | 0.97407 | 0.944 | 0.0037504 | 4.72 | 7.8 | 7.45
17 |  | 17:00 | 0.97963 | 0.956 | 0.0037718 | 4.78 | 7.2 | 7.45
18 |  | 18:00 | 0.98148 | 0.96 | 0.0037789 | 4.8 | 7 | 7.45
19 |  | 19:00 | 0.98241 | 0.962 | 0.0037825 | 4.81 | 6.9 | 7.45
20 |  | 20:00 | 0.98426 | 0.966 | 0.0037896 | 4.83 | 6.7 | 7.45
21 |  | 21:00 | 0.98611 | 0.97 | 0.0037967 | 4.85 | 6.5 | 7.45
22 |  | 22:00 | 0.98704 | 0.972 | 0.0038003 | 4.86 | 6.4 | 7.45
23 |  | 23:00 | 0.98796 | 0.974 | 0.0038039 | 4.87 | 6.3 | 7.45
24 |  | 0:00 | 0.96667 | 0.928 | 0.0037219 | 4.64 | 8.6 | 8.55
25 |  | 1:00 | 0.96481 | 0.924 | 0.0037147 | 4.62 | 8.8 | 8.55
26 |  | 2:00 | 0.96481 | 0.924 | 0.0037147 | 4.62 | 8.8 | 8.55
27 |  | 3:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 8.55
28 |  | 4:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 8.55
29 |  | 5:00 | 0.96296 | 0.92 | 0.0037076 | 4.6 | 9 | 8.55
30 |  | 6:00 | 0.96111 | 0.916 | 0.0037005 | 4.58 | 9.2 | 8.55
31 |  | 7:00 | 0.96204 | 0.918 | 0.003704 | 4.59 | 9.1 | 8.55
32 |  | 8:00 | 0.96019 | 0.914 | 0.0036969 | 4.57 | 9.3 | 8.55
33 |  | 9:00 | 0.95926 | 0.912 | 0.0036933 | 4.56 | 9.4 | 8.55
34 |  | 10:00 | 0.96019 | 0.914 | 0.0036969 | 4.57 | 9.3 | 8.55
35 |  | 11:00 | 0.95926 | 0.912 | 0.0036933 | 4.56 | 9.4 | 8.55
36 |  | 12:00 | 0.96204 | 0.918 | 0.003704 | 4.59 | 9.1 | 8.55
37 |  | 13:00 | 0.95648 | 0.906 | 0.0036826 | 4.53 | 9.7 | 8.55
38 |  | 14:00 | 0.95463 | 0.902 | 0.0036755 | 4.51 | 9.9 | 8.55
39 |  | 15:00 | 0.95463 | 0.902 | 0.0036755 | 4.51 | 9.9 | 8.55
40 |  | 16:00 | 0.95926 | 0.912 | 0.0036933 | 4.56 | 9.4 | 8.55
41 |  | 17:00 | 0.96111 | 0.916 | 0.0037005 | 4.58 | 9.2 | 8.55
42 |  | 18:00 | 0.97037 | 0.936 | 0.0037361 | 4.68 | 8.2 | 8.55
43 |  | 19:00 | 0.97963 | 0.956 | 0.0037718 | 4.78 | 7.2 | 8.55
44 |  | 20:00 | 0.98241 | 0.962 | 0.0037825 | 4.81 | 6.9 | 8.55
45 |  | 21:00 | 0.98611 | 0.97 | 0.0037967 | 4.85 | 6.5 | 8.55
46 |  | 22:00 | 0.99259 | 0.984 | 0.0038217 | 4.92 | 5.8 | 8.55
47 |  | 23:00 | 0.99907 | 0.998 | 0.0038466 | 4.99 | 5.1 | 8.55
48 |  | 0:00 | 0.99722 | 0.994 | 0.0038395 | 4.97 | 5.3 | 9.9833
49 |  | 1:00 | 0.99537 | 0.99 | 0.0038324 | 4.95 | 5.5 | 9.9833
50 |  | 2:00 | 1 | 1 | 0.0038502 | 5 | 5 | 9.9833
51 |  | 3:00 | 0.99907 | 0.998 | 0.0038466 | 4.99 | 5.1 | 9.9833
52 |  | 4:00 | 1.0009 | 1.002 | 0.0038538 | 5.01 | 4.9 | 9.9833
53 |  | 5:00 | 1.0009 | 1.002 | 0.0038538 | 5.01 | 4.9 | 9.9833
54 |  | 6:00 | 0.99722 | 0.994 | 0.0038395 | 4.97 | 5.3 | 9.9833
55 |  | 7:00 | 0.98981 | 0.978 | 0.003811 | 4.89 | 6.1 | 9.9833
56 |  | 8:00 | 0.97222 | 0.94 | 0.0037433 | 4.7 | 8 | 9.9833
57 |  | 9:00 | 0.96019 | 0.914 | 0.0036969 | 4.57 | 9.3 | 9.9833
58 |  | 10:00 | 0.93981 | 0.87 | 0.0036185 | 4.35 | 11.5 | 9.9833
59 |  | 11:00 | 0.95093 | 0.894 | 0.0036613 | 4.47 | 10.3 | 9.9833
60 |  | 12:00 | 0.93056 | 0.85 | 0.0035828 | 4.25 | 12.5 | 9.9833
61 |  | 13:00 | 0.9213 | 0.83 | 0.0035472 | 4.15 | 13.5 | 9.9833
62 |  | 14:00 | 0.9287 | 0.846 | 0.0035757 | 4.23 | 12.7 | 9.9833
63 |  | 15:00 | 0.91667 | 0.82 | 0.0035294 | 4.1 | 14 | 9.9833
64 |  | 16:00 | 0.91111 | 0.808 | 0.003508 | 4.04 | 14.6 | 9.9833
65 |  | 17:00 | 0.91296 | 0.812 | 0.0035151 | 4.06 | 14.4 | 9.9833
66 |  | 18:00 | 0.91111 | 0.808 | 0.003508 | 4.04 | 14.6 | 9.9833
67 |  | 19:00 | 0.91574 | 0.818 | 0.0035258 | 4.09 | 14.1 | 9.9833
68 |  | 20:00 | 0.9213 | 0.83 | 0.0035472 | 4.15 | 13.5 | 9.9833
69 |  | 21:00 | 0.93333 | 0.856 | 0.0035935 | 4.28 | 12.2 | 9.9833
70 |  | 22:00 | 0.94259 | 0.876 | 0.0036292 | 4.38 | 11.2 | 9.9833
71 |  | 23:00 | 0.94352 | 0.878 | 0.0036327 | 4.39 | 11.1 | 9.9833
72 |  | 0:00 | 0.89259 | 0.768 | 0.0034367 | 3.84 | 16.6 | 21.7708
73 |  | 1:00 | 0.88889 | 0.76 | 0.0034224 | 3.8 | 17 | 21.7708
74 |  | 2:00 | 0.89259 | 0.768 | 0.0034367 | 3.84 | 16.6 | 21.7708
75 |  | 3:00 | 0.89815 | 0.78 | 0.0034581 | 3.9 | 16 | 21.7708
76 |  | 4:00 | 0.90278 | 0.79 | 0.0034759 | 3.95 | 15.5 | 21.7708
77 |  | 5:00 | 0.90741 | 0.8 | 0.0034937 | 4 | 15 | 21.7708
78 |  | 6:00 | 0.90833 | 0.802 | 0.0034973 | 4.01 | 14.9 | 21.7708
79 |  | 7:00 | 0.89537 | 0.774 | 0.0034474 | 3.87 | 16.3 | 21.7708
80 |  | 8:00 | 0.88148 | 0.744 | 0.0033939 | 3.72 | 17.8 | 21.7708
81 |  | 9:00 | 0.86204 | 0.702 | 0.003319 | 3.51 | 19.9 | 21.7708
82 |  | 10:00 | 0.84074 | 0.656 | 0.003237 | 3.28 | 22.2 | 21.7708
83 |  | 11:00 | 0.82037 | 0.612 | 0.0031586 | 3.06 | 24.4 | 21.7708
84 |  | 12:00 | 0.83056 | 0.634 | 0.0031978 | 3.17 | 23.3 | 21.7708
85 |  | 13:00 | 0.83519 | 0.644 | 0.0032156 | 3.22 | 22.8 | 21.7708
86 |  | 14:00 | 0.82222 | 0.616 | 0.0031657 | 3.08 | 24.2 | 21.7708
87 |  | 15:00 | 0.82407 | 0.62 | 0.0031729 | 3.1 | 24 | 21.7708
88 |  | 16:00 | 0.81481 | 0.6 | 0.0031372 | 3 | 28.2 | 21.7708
89 |  | 17:00 | 0.81481 | 0.6 | 0.0031372 | 3 | 28.7 | 21.7708
90 |  | 18:00 | 0.81481 | 0.6 | 0.0031372 | 3 | 28.6 | 21.7708
91 |  | 19:00 | 0.81481 | 0.6 | 0.0031372 | 3 | 27.8 | 21.7708
92 |  | 20:00 | 0.81481 | 0.6 | 0.0031372 | 3 | 27.2 | 21.7708
93 |  | 21:00 | 0.81481 | 0.6 | 0.0031372 | 3 | 26.4 | 21.7708
94 |  | 22:00 | 0.81574 | 0.602 | 0.0031408 | 3.01 | 24.9 | 21.7708
95 |  | 23:00 | 0.82222 | 0.616 | 0.0031657 | 3.08 | 24.2 | 21.7708
96 |  | 0:00 | 0.87407 | 0.728 | 0.0033654 | 3.64 | 18.6 | 19.35
97 |  | 1:00 | 0.87315 | 0.726 | 0.0033618 | 3.63 | 18.7 | 19.35
98 |  | 2:00 | 0.87593 | 0.732 | 0.0033725 | 3.66 | 18.4 | 19.35
99 |  | 3:00 | 0.875 | 0.73 | 0.0033689 | 3.65 | 18.5 | 19.35
100 |  | 4:00 | 0.87685 | 0.734 | 0.0033761 | 3.67 | 18.3 | 19.35
101 |  | 5:00 | 0.87963 | 0.74 | 0.0033868 | 3.7 | 18 | 19.35
102 |  | 6:00 | 0.87963 | 0.74 | 0.0033868 | 3.7 | 18 | 19.35
103 |  | 7:00 | 0.88704 | 0.756 | 0.0034153 | 3.78 | 17.2 | 19.35
104 |  | 8:00 | 0.8787 | 0.738 | 0.0033832 | 3.69 | 18.1 | 19.35
105 |  | 9:00 | 0.87315 | 0.726 | 0.0033618 | 3.63 | 18.7 | 19.35
106 |  | 10:00 | 0.86852 | 0.716 | 0.003344 | 3.58 | 19.2 | 19.35
107 |  | 11:00 | 0.86019 | 0.698 | 0.0033119 | 3.49 | 20.1 | 19.35
108 |  | 12:00 | 0.85741 | 0.692 | 0.0033012 | 3.46 | 20.4 | 19.35
109 |  | 13:00 | 0.88241 | 0.746 | 0.0033974 | 3.73 | 17.7 | 19.35
110 |  | 14:00 | 0.86019 | 0.698 | 0.0033119 | 3.49 | 20.1 | 19.35
111 |  | 15:00 | 0.84537 | 0.666 | 0.0032548 | 3.33 | 21.7 | 19.35
112 |  | 16:00 | 0.84444 | 0.664 | 0.0032513 | 3.32 | 21.8 | 19.35
113 |  | 17:00 | 0.84352 | 0.662 | 0.0032477 | 3.31 | 21.9 | 19.35
114 |  | 18:00 | 0.84722 | 0.67 | 0.003262 | 3.35 | 21.5 | 19.35
115 |  | 19:00 | 0.8537 | 0.684 | 0.0032869 | 3.42 | 20.8 | 19.35
116 |  | 20:00 | 0.86296 | 0.704 | 0.0033226 | 3.52 | 19.8 | 19.35
117 |  | 21:00 | 0.87037 | 0.72 | 0.0033511 | 3.6 | 19 | 19.35
118 |  | 22:00 | 0.87037 | 0.72 | 0.0033511 | 3.6 | 19 | 19.35
119 |  | 23:00 | 0.8713 | 0.722 | 0.0033547 | 3.61 | 18.9 | 19.35
120 |  | 0:00 | 0.89722 | 0.778 | 0.0034545 | 3.89 | 16.1 | 16.4875
121 |  | 1:00 | 0.89815 | 0.78 | 0.0034581 | 3.9 | 16 | 16.4875
122 |  | 2:00 | 0.89907 | 0.782 | 0.0034616 | 3.91 | 15.9 | 16.4875
123 |  | 3:00 | 0.89907 | 0.782 | 0.0034616 | 3.91 | 15.9 | 16.4875
124 |  | 4:00 | 0.9 | 0.784 | 0.0034652 | 3.92 | 15.8 | 16.4875
125 |  | 5:00 | 0.90093 | 0.786 | 0.0034687 | 3.93 | 15.7 | 16.4875
126 |  | 6:00 | 0.9 | 0.784 | 0.0034652 | 3.92 | 15.8 | 16.4875
127 |  | 7:00 | 0.90093 | 0.786 | 0.0034687 | 3.93 | 15.7 | 16.4875
128 |  | 8:00 | 0.90093 | 0.786 | 0.0034687 | 3.93 | 15.7 | 16.4875
129 |  | 9:00 | 0.90093 | 0.786 | 0.0034687 | 3.93 | 15.7 | 16.4875
130 |  | 10:00 | 0.89815 | 0.78 | 0.0034581 | 3.9 | 16 | 16.4875
131 |  | 11:00 | 0.89722 | 0.778 | 0.0034545 | 3.89 | 16.1 | 16.4875
132 |  | 12:00 | 0.88241 | 0.746 | 0.0033974 | 3.73 | 17.7 | 16.4875
133 |  | 13:00 | 0.89074 | 0.764 | 0.0034295 | 3.82 | 16.8 | 16.4875
134 |  | 14:00 | 0.88056 | 0.742 | 0.0033903 | 3.71 | 17.9 | 16.4875
135 |  | 15:00 | 0.86944 | 0.718 | 0.0033475 | 3.59 | 19.1 | 16.4875
136 |  | 16:00 | 0.86944 | 0.718 | 0.0033475 | 3.59 | 19.1 | 16.4875
137 |  | 17:00 | 0.87593 | 0.732 | 0.0033725 | 3.66 | 18.4 | 16.4875
138 |  | 18:00 | 0.87407 | 0.728 | 0.0033654 | 3.64 | 18.6 | 16.4875
139 |  | 19:00 | 0.88426 | 0.75 | 0.0034046 | 3.75 | 17.5 | 16.4875
140 |  | 20:00 | 0.90185 | 0.788 | 0.0034723 | 3.94 | 15.6 | 16.4875
141 |  | 21:00 | 0.90741 | 0.8 | 0.0034937 | 4 | 15 | 16.4875
142 |  | 22:00 | 0.91852 | 0.824 | 0.0035365 | 4.12 | 13.8 | 16.4875
143 |  | 23:00 | 0.9 | 0.784 | 0.0034652 | 3.92 | 15.8 | 16.4875
144 |  | 0:00 | 0.98056 | 0.958 | 0.0037753 | 4.79 | 7.1 | 7.675
145 |  | 1:00 | 0.98333 | 0.964 | 0.003786 | 4.82 | 6.8 | 7.675
146 |  | 2:00 | 0.98981 | 0.978 | 0.003811 | 4.89 | 6.1 | 7.675
147 |  | 3:00 | 0.98889 | 0.976 | 0.0038074 | 4.88 | 6.2 | 7.675
148 |  | 4:00 | 0.98981 | 0.978 | 0.003811 | 4.89 | 6.1 | 7.675
149 |  | 5:00 | 0.97963 | 0.956 | 0.0037718 | 4.78 | 7.2 | 7.675
150 |  | 6:00 | 0.97593 | 0.948 | 0.0037575 | 4.74 | 7.6 | 7.675
151 |  | 7:00 | 0.97222 | 0.94 | 0.0037433 | 4.7 | 8 | 7.675
152 |  | 8:00 | 0.975 | 0.946 | 0.0037539 | 4.73 | 7.7 | 7.675
153 |  | 9:00 | 0.96944 | 0.934 | 0.0037326 | 4.67 | 8.3 | 7.675
154 |  | 10:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 7.675
155 |  | 11:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 7.675
156 |  | 12:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 7.675
157 |  | 13:00 | 0.96944 | 0.934 | 0.0037326 | 4.67 | 8.3 | 7.675
158 |  | 14:00 | 0.96852 | 0.932 | 0.003729 | 4.66 | 8.4 | 7.675
159 |  | 15:00 | 0.9713 | 0.938 | 0.0037397 | 4.69 | 8.1 | 7.675
160 |  | 16:00 | 0.96944 | 0.934 | 0.0037326 | 4.67 | 8.3 | 7.675
161 |  | 17:00 | 0.96481 | 0.924 | 0.0037147 | 4.62 | 8.8 | 7.675
162 |  | 18:00 | 0.96111 | 0.916 | 0.0037005 | 4.58 | 9.2 | 7.675
163 |  | 19:00 | 0.97315 | 0.942 | 0.0037468 | 4.71 | 7.9 | 7.675
164 |  | 20:00 | 0.97778 | 0.952 | 0.0037646 | 4.76 | 7.4 | 7.675
165 |  | 21:00 | 0.97963 | 0.956 | 0.0037718 | 4.78 | 7.2 | 7.675
166 |  | 22:00 | 0.98241 | 0.962 | 0.0037825 | 4.81 | 6.9 | 7.675
167 |  | 23:00 | 0.98611 | 0.97 | 0.0037967 | 4.85 | 6.5 | 7.675
168 |  | 0:00 | 0.96667 | 0.928 | 0.0037219 | 4.64 | 8.6 | 8.4042
169 |  | 1:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 8.4042
170 |  | 2:00 | 0.96389 | 0.922 | 0.0037112 | 4.61 | 8.9 | 8.4042
171 |  | 3:00 | 0.96574 | 0.926 | 0.0037183 | 4.63 | 8.7 | 8.4042
172 |  | 4:00 | 0.96852 | 0.932 | 0.003729 | 4.66 | 8.4 | 8.4042
173 |  | 5:00 | 0.97037 | 0.936 | 0.0037361 | 4.68 | 8.2 | 8.4042
174 |  | 6:00 | 0.96852 | 0.932 | 0.003729 | 4.66 | 8.4 | 8.4042
175 |  | 7:00 | 0.97685 | 0.95 | 0.0037611 | 4.75 | 7.5 | 8.4042
176 |  | 8:00 | 0.97778 | 0.952 | 0.0037646 | 4.76 | 7.4 | 8.4042
177 |  | 9:00 | 0.96944 | 0.934 | 0.0037326 | 4.67 | 8.3 | 8.4042
178 |  | 10:00 | 0.9713 | 0.938 | 0.0037397 | 4.69 | 8.1 | 8.4042
179 |  | 11:00 | 0.96944 | 0.934 | 0.0037326 | 4.67 | 8.3 | 8.4042
180 |  | 12:00 | 0.96759 | 0.93 | 0.0037254 | 4.65 | 8.5 | 8.4042
181 |  | 13:00 | 0.96481 | 0.924 | 0.0037147 | 4.62 | 8.8 | 8.4042
182 |  | 14:00 | 0.96481 | 0.924 | 0.0037147 | 4.62 | 8.8 | 8.4042
183 |  | 15:00 | 0.96389 | 0.922 | 0.0037112 | 4.61 | 8.9 | 8.4042
184 |  | 16:00 | 0.96852 | 0.932 | 0.003729 | 4.66 | 8.4 | 8.4042
185 |  | 17:00 | 0.96852 | 0.932 | 0.003729 | 4.66 | 8.4 | 8.4042
186 |  | 18:00 | 0.97037 | 0.936 | 0.0037361 | 4.68 | 8.2 | 8.4042
187 |  | 19:00 | 0.9713 | 0.938 | 0.0037397 | 4.69 | 8.1 | 8.4042
188 |  | 20:00 | 0.96759 | 0.93 | 0.0037254 | 4.65 | 8.5 | 8.4042
189 |  | 21:00 | 0.96296 | 0.92 | 0.0037076 | 4.6 | 9 | 8.4042
190 |  | 22:00 | 0.96667 | 0.928 | 0.0037219 | 4.64 | 8.6 | 8.4042
191 |  | 23:00 | 0.97222 | 0.94 | 0.0037433 | 4.7 | 8 | 8.4042

## Demand
| TR [⁰C] | Tmin [⁰C] | Q0 [m3/s] | Qmax [m3/s]
Industrial P2G | 25 | 5 | 0.0031372 | 0.0038502
District Heating P2H | 25 | 5 | 3 | 4
Q(t) = Q0+((Qmax-Q0)/(TR-Tmin))* max(0,TR-T(t))
| 3.565e-05 | 0.05
5

## Flexibility Deployment
Price Signals for PP
Variables
|  | Efficiency (η) | LC of Energy
| P2G | input from model | Levelized Cost of Hydrogen Production
| P2H | input from model | Levelized Cost of Heat Production
LCOE
|  |  | Electrolyser | HP | Boiler | Hot Water Storage | Hydrogen Storage
| Capital costs (CAPEX) |  | 200 EUR/kW | 1000 EUR/kW | 70 EUR/kW | 1040 EUR/m3 | 6.24 EUR/kg
| Operation & maintenance costs |  | 8 EUR/kW | 33.5 EUR /kW | 1.4 EUR/kW | 1.3 EUR/m3 | 0.12 EUR/kg
| Lifetime |  | 20 years | 20 years | 15 years | 20 years | 30 years
| Fuel cost |  | Green Electricity
Emission reduction rate (?)
Carbon cost
|  | time constant | 10s
|  | efficiency | 0.6-0.78 | COP 4-7 | 99
|  |  | 34.6154 | 23.6258 | 4.8081
0.0046111
(((CAP+ O&M)/(LT))+Carbon penalty)/efficiency cost [EUR/kW]
0.0173
|  |  | wind electrolysis | 16.6 | g CO2/kWh | 1 | EUR/g CO2
|  |  | solar electrolysis | 42.4 | g CO2/kWh | 1 | EUR/g CO2
|  |  | Heat Pump | 62.28 | g CO2/kwh
61.92
[5 empty] | €€€ | 0.0044611
0.0046111
0.0173
|  |  | total greenhouse gas emission of the pathway |  |  |  |  | e
The penalty cost due to CO2 emission (Cenv) of the heat pump system can be calculated as follows:

## Storage
P2G |  |  |  | P2H
molar mass | 2.016*10-3 |  |  | mass flow
specific heat
density | 0.06953 | at 30 bar | at 80 C | density
| 20.2742 | at 350 bar | at 80C