## HP Calculations
Tevaporation
|  | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44 | at 70 celcius |  |  |  | at 50 celcius
| H1 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 |  |  |  | P2=P3 | 2.1168 | MPa |  | P2=P3 | 1.3179 | MPa
| H2 | 386.55 | 389.02 | 391.46 | 393.87 | 396.25 | 398.6 | 400.92 | 403.2 | 405.43 | 407.61 | 409.75 | 411.82 | 413.84 | 415.78 | 417.65 | 419.43 | 421.11 | H4 | 428.65 | kj/kg |  | H4 | 423.44 | kj/kg
| S2=S1 | 1.7413 | 1.7379 | 1.7348 | 1.732 | 1.7294 | 1.7271 | 1.725 | 1.723 | 1.7212 | 1.7196 | 1.718 | 1.7166 | 1.7152 | 1.7138 | 1.7124 | 1.7111 | 1.7096 | H5 | 304.28 |  |  | H5 | 271.62
| H3 at 70 | 444.5933 | 443.3907 | 442.2941 | 441.3037 | 440.3884 | 439.5859 | 438.8532 | 438.1554 | 437.5274 | 436.9691 | 436.4109 | 435.9224 | 435.4339 | 434.9455 | 434.457 | 434.0034 | 433.4801 | S4 | 1.6956 | kj/kg.K |  | S4 | 1.7072 | kj/kg.K
| H3 at 50 | 434.5756 | 433.4406 | 432.4058 | 431.4844 | 430.6294 | 429.873 | 429.1824 | 428.5246 | 427.9372 | 427.4163 | 426.8953 | 426.4395 | 425.9837 | 425.5278 | 425.072 | 424.6487 | 424.1603 | S5 | 1.3332 |  |  | S5 | 1.2375
|  | pressure | 2 | [6 empty] | Pressure | 2.2 | [6 empty] | pressure | 2.1168 |  |  | pressure | 1.2 |  |  | Pressure | 1.4
|  | Temp | H | S | [5 empty] | Temp | H | S | [5 empty] | Temp3 | H3 |  |  | Temp | H | S |  | Temp | H | S
|  | 67.49 | 428.52 | 1.6983 | [5 empty] | 71.74 | 429.08 | 1.6948 | [9 empty] | 46.32 | 422.22 | 1.7092 |  | 52.43 | 424.5 | 1.7068
|  | 70 | 432.22 | 1.7091 | [17 empty] | 50 | 426.51 | 1.7226 |  | 60 | 433.69 | 1.7347
|  | 80 | 445.86 | 1.7483 | [5 empty] | 80 | 441.49 | 1.7303 | [9 empty] | 60 | 437.83 | 1.7571 |  | 70 | 445.31 | 1.7691
|  | 90 | 458.49 | 1.7835 | [5 empty] | 90 | 454.98 | 1.768 | [9 empty] | 70 |  |  |  | 80
|  | 100 | [7 empty] | 100 | 467.61 | 1.8023 | [9 empty] | 80 |  |  |  | 90
Linear interpolatation
H3 calculator
| at S70,p=2 | 443.4243 | 442.2412 | 441.1626 | 440.1883 | 439.2836 | 438.4833 | 437.7526 | 437.0566 | 436.4303 | 435.8736 | 435.3168 | 434.8297 | 434.3426 | 433.8554 | 433.3683 | 432.9159 | 432.394
| at S50, p = 1.2 | 432.6458 | 431.5302 | 430.513 | 429.5943 | 428.7412 | 427.9865 | 427.2975 | 426.6412 | 426.0618 | 425.5496 | 425.0373 | 424.5891 | 424.1409 | 423.6927 | 423.2445 | 422.8283 | 422.3481
Results
W (kj/kg) | H3-H2 | 58.0433 | 54.3707 | 50.8341 | 47.4337 | 44.1384 | 40.9859 | 37.9332 | 34.9554 | 32.0974 | 29.3591 | 26.6609 | 24.1024 | 21.5939 | 19.1655 | 16.807 | 14.5734 | 12.3701
Q(kj/kg) | H3-H5 | 140.3133 | 139.1107 | 138.0141 | 137.0237 | 136.1084 | 135.3059 | 134.5732 | 133.8754 | 133.2474 | 132.6891 | 132.1309 | 131.6424 | 131.1539 | 130.6655 | 130.177 | 129.7234 | 129.2001
COP at 70 | Q/W | 2.4174 | 2.5586 | 2.715 | 2.8887 | 3.0837 | 3.3013 | 3.5476 | 3.8299 | 4.1513 | 4.5195 | 4.956 | 5.4618 | 6.0736 | 6.8178 | 7.7454 | 8.9014 | 10.4446
COP at 50 |  | 3.3931 | 3.6429 | 3.9268 | 4.2501 | 4.6251 | 5.0604 | 5.575 | 6.1957 | 6.9452 | 7.866 | 9.0564 | 10.5899 | 12.7115 | 15.7889 | 20.6753 | 29.3231 | 50.008
cycle efficiency | COP(Tcon-Teva)/Teva | 0.85943 | 0.85567 | 0.8525 | 0.84979 | 0.84782 | 0.84602 | 0.84483 | 0.84458 | 0.84439 | 0.84404 | 0.8453 | 0.84551 | 0.84706 | 0.84901 | 0.85183 | 0.85276 | 0.85625
| at 50 | 0.93825 | 0.93499 | 0.93227 | 0.92968 | 0.92795 | 0.9263 | 0.92531 | 0.92556 | 0.92554 | 0.92493 | 0.9268 | 0.9266 | 0.92861 | 0.93135 | 0.93629 | 0.93639 | 0.94608
m(kg/s) | 50000(kW)/(Q) | 356.3453 | 359.426 | 362.2817 | 364.9003 | 367.3543 | 369.533 | 371.545 | 373.4816 | 375.2419 | 376.8206 | 378.4127 | 379.8168 | 381.2314 | 382.6565 | 384.0924 | 385.4354 | 386.9967
W (kj/kg) | H3-H2 | 48.0256 | 44.4206 | 40.9458 | 37.6144 | 34.3794 | 31.273 | 28.2624 | 25.3246 | 22.5072 | 19.8063 | 17.1453 | 14.6195 | 12.1437 | 9.7478 | 7.422 | 5.2187 | 3.0503
Q(kj/kg) | H3-H5 | 162.9556 | 161.8206 | 160.7858 | 159.8644 | 159.0094 | 158.253 | 157.5624 | 156.9046 | 156.3172 | 155.7963 | 155.2753 | 154.8195 | 154.3637 | 153.9078 | 153.452 | 153.0287 | 152.5403
| at S70,p=2.2 | 445.4261 | 444.2095 | 443.1002 | 442.0983 | 441.1754 | 440.3714 | 439.6372 | 438.9381 | 438.3088 | 437.7495 | 437.1902 | 436.7008 | 436.2114 | 435.722 | 435.2326 | 434.7781 | 434.2537
| at S50, p = 1.4 | 435.9194 | 434.7709 | 433.7238 | 432.8006 | 431.9442 | 431.1866 | 430.4949 | 429.8361 | 429.2432 | 428.7162 | 428.1892 | 427.728 | 427.2669 | 426.8057 | 426.3446 | 425.9164 | 425.4223
| final at 70 | 444.5933 | 443.3907 | 442.2941 | 441.3037 | 440.3884 | 439.5859 | 438.8532 | 438.1554 | 437.5274 | 436.9691 | 436.4109 | 435.9224 | 435.4339 | 434.9455 | 434.457 | 434.0034 | 433.4801
| final at 50 | 434.5756 | 433.4406 | 432.4058 | 431.4844 | 430.6294 | 429.873 | 429.1824 | 428.5246 | 427.9372 | 427.4163 | 426.8953 | 426.4395 | 425.9837 | 425.5278 | 425.072 | 424.6487 | 424.1603

## p-H cycle table
1
2
3
4
5

## photo
1
2
3
4
5

## COPat50 vs. Teva
Teva |  | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
COP at 50
|  | 3.3931 | 3.6429 | 3.9268 | 4.2501 | 4.6251 | 5.0604 | 5.575 | 6.1957 | 6.9452 | 7.866 | 9.0564 | 10.5899 | 12.7115 | 15.7889 | 20.6753 | 29.3231 | 50.008
| -20 | 3.3931
| -16 | 3.6429
| -12 | 3.9268
| -8 | 4.2501 | [13 empty] | Linear model Poly5: f(x) = p1*x^5 + p2*x^4 + p3*x^3 + p4*x^2 + p5*x + p6 Coefficients (with 95% confidence bounds): p1 = 3.461e-08 (2.389e-08, 4.533e-08) p2 = 1.29e-06 (1.131e-06, 1.449e-06) p3 = 4.353e-05 (3.721e-05, 4.984e-05) p4 = 0.002387 (0.002319, 0.002455) p5 = 0.1186 (0.1178, 0.1195) p6 = 5.063 (5.057, 5.068) Goodness of fit: SSE: 8.541e-05 R-square: 1 Adjusted R-square: 1 RMSE: 0.003773
| -4 | 4.6251
| 0 | 5.0604
| 4 | 5.575
| 8 | 6.1957
| 12 | 6.9452
| 16 | 7.866
| 20 | 9.0564
| 24 | 10.5899
| 28 | 12.7115
| 32 | 15.7889
| 36 | 20.6753
| 40 | 29.3231
| 44 | 50.008

## COPat70 vs. Teva
Teva | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
COP
| 2.4174 | 2.5586 | 2.715 | 2.8887 | 3.0837 | 3.3013 | 3.5476 | 3.8299 | 4.1513 | 4.5195 | 4.956 | 5.4618 | 6.0736 | 6.8178 | 7.7454 | 8.9014 | 10.4446
5th order polynomial function
Linear model Poly5: f(x) = p1*x^5 + p2*x^4 + p3*x^3 + p4*x^2 + p5*x + p6 Coefficients (with 95% confidence bounds): p1 = 1.457e-08 (1.116e-08, 1.798e-08) p2 = -9.658e-08 (-3.086e-07, 1.154e-07) p3 = 6.609e-06 (3.71e-06, 9.508e-06) p4 = 0.00101 (0.000908, 0.001112) p5 = 0.05864 (0.05748, 0.05979) p6 = 3.295 (3.284, 3.306) Goodness of fit: SSE: 0.001116 R-square: 1 Adjusted R-square: 1 RMSE: 0.01007
| x | y
| -20 | 2.4174
| -16 | 2.5586
| -12 | 2.715
| -8 | 2.8887
| -4 | 3.0837
| 0 | 3.3013
| 4 | 3.5476
| 8 | 3.8299
| 12 | 4.1513
| 16 | 4.5195
| 20 | 4.956
| 24 | 5.4618
| 28 | 6.0736
| 32 | 6.8178
| 36 | 7.7454
| 40 | 8.9014
| 44 | 10.4446

## P2H Models
Modelling Considerations of P2H
Model | Modelling Approach | Dynamic Behaviour | Modelling Scale | COP
A | Regression | Linear | HP | Constant
B | Regression | Non-linear | HP | Variable
C | Regression | Non-linear | HP with auxiliary boiler | Constant
Tcondenser | a1 | a2 | a3 | a4 | a5 | a6
50 | 3.461e-08 | 1.29e-06 | 4.353e-05 | 0.002387 | 0.1186 | 5.063
70 | 1.457e-08 | -9.658e-08 | 6.609e-06 | 0.00101 | 0.05864 | 3.295

## Boiler
Q | m*c*∆T(40-Twaste)
η | efficiency | 0.99
W | Q/η
m | mass/massflow R134a | 390 | kg/s
c | specific heat capacity | 1.3215 | kJ/(kg.K) | at 40 celcius quality=0.5
Tevaporation
| -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
H1 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28
H2 | 386.55 | 389.02 | 391.46 | 393.87 | 396.25 | 398.6 | 400.92 | 403.2 | 405.43 | 407.61 | 409.75 | 411.82 | 413.84 | 415.78 | 417.65 | 419.43 | 421.11
H2-H1 | 82.27 | 84.74 | 87.18 | 89.59 | 91.97 | 94.32 | 96.64 | 98.92 | 101.15 | 103.33 | 105.47 | 107.54 | 109.56 | 111.5 | 113.37 | 115.15 | 116.83
|  | Tamb | Q
|  | -20 | 82.27
|  | -16 | 84.74
|  | -12 | 87.18
|  | -8 | 89.59
|  | -4 | 91.97
|  | 0 | 94.32
|  | 4 | 96.64
|  | 8 | 98.92
|  | 12 | 101.15
|  | 16 | 103.33
|  | 20 | 105.47
|  | 24 | 107.54
|  | 28 | 109.56
|  | 32 | 111.5
|  | 36 | 113.37
|  | 40 | 115.15
|  | 44 | 116.83

## Tamb
Weather archive in Hoek Van Holland weather station number :06330 https://rp5.ru/Weather_archive_in_Hoek_Van_Holland
Ambient Air temperature at 2m
Hour\Day | 2019-02-07 |  |  | 2019-03-23 |  |  | 2019-05-07 |  |  | 2019-06-23
| Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s)
0:00 | 6.8 | 0.003786 | 4.82 | 8.6 | 0.0037219 | 4.64 | 5.3 | 0.0038395 | 4.97 | 16.6 | 0.0034367 | 3.84
1:00 | 6.9 | 0.0037825 | 4.81 | 8.8 | 0.0037147 | 4.62 | 5.5 | 0.0038324 | 4.95 | 17 | 0.0034224 | 3.8
2:00 | 7.3 | 0.0037682 | 4.77 | 8.8 | 0.0037147 | 4.62 | 5 | 0.0038502 | 5 | 16.6 | 0.0034367 | 3.84
3:00 | 7.8 | 0.0037504 | 4.72 | 8.7 | 0.0037183 | 4.63 | 5.1 | 0.0038466 | 4.99 | 16 | 0.0034581 | 3.9
4:00 | 8.1 | 0.0037397 | 4.69 | 8.7 | 0.0037183 | 4.63 | 4.9 | 0.0038538 | 5.01 | 15.5 | 0.0034759 | 3.95
5:00 | 8.8 | 0.0037147 | 4.62 | 9 | 0.0037076 | 4.6 | 4.9 | 0.0038538 | 5.01 | 15 | 0.0034937 | 4
6:00 | 9 | 0.0037076 | 4.6 | 9.2 | 0.0037005 | 4.58 | 5.3 | 0.0038395 | 4.97 | 14.9 | 0.0034973 | 4.01
7:00 | 7.4 | 0.0037646 | 4.76 | 9.1 | 0.003704 | 4.59 | 6.1 | 0.003811 | 4.89 | 16.3 | 0.0034474 | 3.87
8:00 | 6.8 | 0.003786 | 4.82 | 9.3 | 0.0036969 | 4.57 | 8 | 0.0037433 | 4.7 | 17.8 | 0.0033939 | 3.72
9:00 | 6.7 | 0.0037896 | 4.83 | 9.4 | 0.0036933 | 4.56 | 9.3 | 0.0036969 | 4.57 | 19.9 | 0.003319 | 3.51
10:00 | 7.1 | 0.0037753 | 4.79 | 9.3 | 0.0036969 | 4.57 | 11.5 | 0.0036185 | 4.35 | 22.2 | 0.003237 | 3.28
11:00 | 7.8 | 0.0037504 | 4.72 | 9.4 | 0.0036933 | 4.56 | 10.3 | 0.0036613 | 4.47 | 24.4 | 0.0031586 | 3.06
12:00 | 8.1 | 0.0037397 | 4.69 | 9.1 | 0.003704 | 4.59 | 12.5 | 0.0035828 | 4.25 | 23.3 | 0.0031978 | 3.17
13:00 | 8.6 | 0.0037219 | 4.64 | 9.7 | 0.0036826 | 4.53 | 13.5 | 0.0035472 | 4.15 | 22.8 | 0.0032156 | 3.22
14:00 | 8.6 | 0.0037219 | 4.64 | 9.9 | 0.0036755 | 4.51 | 12.7 | 0.0035757 | 4.23 | 24.2 | 0.0031657 | 3.08
15:00 | 8.2 | 0.0037361 | 4.68 | 9.9 | 0.0036755 | 4.51 | 14 | 0.0035294 | 4.1 | 24 | 0.0031729 | 3.1
16:00 | 7.8 | 0.0037504 | 4.72 | 9.4 | 0.0036933 | 4.56 | 14.6 | 0.003508 | 4.04 | 28.2 | 0.0031372 | 3
17:00 | 7.2 | 0.0037718 | 4.78 | 9.2 | 0.0037005 | 4.58 | 14.4 | 0.0035151 | 4.06 | 28.7 | 0.0031372 | 3
18:00 | 7 | 0.0037789 | 4.8 | 8.2 | 0.0037361 | 4.68 | 14.6 | 0.003508 | 4.04 | 28.6 | 0.0031372 | 3
19:00 | 6.9 | 0.0037825 | 4.81 | 7.2 | 0.0037718 | 4.78 | 14.1 | 0.0035258 | 4.09 | 27.8 | 0.0031372 | 3
20:00 | 6.7 | 0.0037896 | 4.83 | 6.9 | 0.0037825 | 4.81 | 13.5 | 0.0035472 | 4.15 | 27.2 | 0.0031372 | 3
21:00 | 6.5 | 0.0037967 | 4.85 | 6.5 | 0.0037967 | 4.85 | 12.2 | 0.0035935 | 4.28 | 26.4 | 0.0031372 | 3
22:00 | 6.4 | 0.0038003 | 4.86 | 5.8 | 0.0038217 | 4.92 | 11.2 | 0.0036292 | 4.38 | 24.9 | 0.0031408 | 3.01
23:00 | 6.3 | 0.0038039 | 4.87 | 5.1 | 0.0038466 | 4.99 | 11.1 | 0.0036327 | 4.39 | 24.2 | 0.0031657 | 3.08
Average | 7.45 | 0.0037629 | 4.755 | 8.55 | 0.0037236 | 4.645 | 9.9833 | 0.0036725 | 4.5017 | 21.7708 | 0.0032774 | 3.3933
Hour\Day | 2019-08-07 |  |  | 2019-09-23 |  |  | 2019-11-07 |  |  | 2019-12-23
| Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s) | Tamb (⁰C) | Industrial Hydrogen Demand (m3/s) | DHN Demand (m3/s)
0:00 | 18.6 | 0.0033654 | 3.64 | 16.1 | 0.0034545 | 3.89 | 7.1 | 0.0037753 | 4.79 | 8.6 | 0.0037219 | 4.64
1:00 | 18.7 | 0.0033618 | 3.63 | 16 | 0.0034581 | 3.9 | 6.8 | 0.003786 | 4.82 | 8.7 | 0.0037183 | 4.63
2:00 | 18.4 | 0.0033725 | 3.66 | 15.9 | 0.0034616 | 3.91 | 6.1 | 0.003811 | 4.89 | 8.9 | 0.0037112 | 4.61
3:00 | 18.5 | 0.0033689 | 3.65 | 15.9 | 0.0034616 | 3.91 | 6.2 | 0.0038074 | 4.88 | 8.7 | 0.0037183 | 4.63
4:00 | 18.3 | 0.0033761 | 3.67 | 15.8 | 0.0034652 | 3.92 | 6.1 | 0.003811 | 4.89 | 8.4 | 0.003729 | 4.66
5:00 | 18 | 0.0033868 | 3.7 | 15.7 | 0.0034687 | 3.93 | 7.2 | 0.0037718 | 4.78 | 8.2 | 0.0037361 | 4.68
6:00 | 18 | 0.0033868 | 3.7 | 15.8 | 0.0034652 | 3.92 | 7.6 | 0.0037575 | 4.74 | 8.4 | 0.003729 | 4.66
7:00 | 17.2 | 0.0034153 | 3.78 | 15.7 | 0.0034687 | 3.93 | 8 | 0.0037433 | 4.7 | 7.5 | 0.0037611 | 4.75
8:00 | 18.1 | 0.0033832 | 3.69 | 15.7 | 0.0034687 | 3.93 | 7.7 | 0.0037539 | 4.73 | 7.4 | 0.0037646 | 4.76
9:00 | 18.7 | 0.0033618 | 3.63 | 15.7 | 0.0034687 | 3.93 | 8.3 | 0.0037326 | 4.67 | 8.3 | 0.0037326 | 4.67
10:00 | 19.2 | 0.003344 | 3.58 | 16 | 0.0034581 | 3.9 | 8.7 | 0.0037183 | 4.63 | 8.1 | 0.0037397 | 4.69
11:00 | 20.1 | 0.0033119 | 3.49 | 16.1 | 0.0034545 | 3.89 | 8.7 | 0.0037183 | 4.63 | 8.3 | 0.0037326 | 4.67
12:00 | 20.4 | 0.0033012 | 3.46 | 17.7 | 0.0033974 | 3.73 | 8.7 | 0.0037183 | 4.63 | 8.5 | 0.0037254 | 4.65
13:00 | 17.7 | 0.0033974 | 3.73 | 16.8 | 0.0034295 | 3.82 | 8.3 | 0.0037326 | 4.67 | 8.8 | 0.0037147 | 4.62
14:00 | 20.1 | 0.0033119 | 3.49 | 17.9 | 0.0033903 | 3.71 | 8.4 | 0.003729 | 4.66 | 8.8 | 0.0037147 | 4.62
15:00 | 21.7 | 0.0032548 | 3.33 | 19.1 | 0.0033475 | 3.59 | 8.1 | 0.0037397 | 4.69 | 8.9 | 0.0037112 | 4.61
16:00 | 21.8 | 0.0032513 | 3.32 | 19.1 | 0.0033475 | 3.59 | 8.3 | 0.0037326 | 4.67 | 8.4 | 0.003729 | 4.66
17:00 | 21.9 | 0.0032477 | 3.31 | 18.4 | 0.0033725 | 3.66 | 8.8 | 0.0037147 | 4.62 | 8.4 | 0.003729 | 4.66
18:00 | 21.5 | 0.003262 | 3.35 | 18.6 | 0.0033654 | 3.64 | 9.2 | 0.0037005 | 4.58 | 8.2 | 0.0037361 | 4.68
19:00 | 20.8 | 0.0032869 | 3.42 | 17.5 | 0.0034046 | 3.75 | 7.9 | 0.0037468 | 4.71 | 8.1 | 0.0037397 | 4.69
20:00 | 19.8 | 0.0033226 | 3.52 | 15.6 | 0.0034723 | 3.94 | 7.4 | 0.0037646 | 4.76 | 8.5 | 0.0037254 | 4.65
21:00 | 19 | 0.0033511 | 3.6 | 15 | 0.0034937 | 4 | 7.2 | 0.0037718 | 4.78 | 9 | 0.0037076 | 4.6
22:00 | 19 | 0.0033511 | 3.6 | 13.8 | 0.0035365 | 4.12 | 6.9 | 0.0037825 | 4.81 | 8.6 | 0.0037219 | 4.64
23:00 | 18.9 | 0.0033547 | 3.61 | 15.8 | 0.0034652 | 3.92 | 6.5 | 0.0037967 | 4.85 | 8 | 0.0037433 | 4.7
Average | 19.35 | 0.0033386 | 3.565 | 16.4875 | 0.0034407 | 3.8513 | 7.675 | 0.0037548 | 4.7325 | 8.4042 | 0.0037288 | 4.6596
|  | slope hydrogen | 3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05
3.565e-05

## Demand
| TReference | Tmin | m0 [m3/s] | mmax [m3/s]
Industrial PtG | 25 | 5 | 0.0031372 | 0.0038502
District Heating PtH | 25 | 5 | 3 | 5
Q(t) = Q0+((Qmax-Q0)/(TR-Tmin))* max(0,TR-T(t))
| 3.565e-05 | 0.1

## Flexibility Deployment
Price Signals for PP
Variables
|  | Efficiency (η) | LC of Energy
| P2G | input from model | Levelized Cost of Hydrogen Production
| P2H | input from model | Levelized Cost of Heat Production
LCOE
|  |  | Electrolyser | HP | Boiler | Hot Water Storage | Hydrogen Storage
| Capital costs (CAPEX) |  | 200 EUR/kW | 1000 EUR/kW | 70 EUR/kW | 1040 EUR/m3 | 6.24 EUR/kg
| Operation & maintenance costs |  | 8 EUR/kW | 33.5 EUR /kW | 1.4 EUR/kW | 1.3 EUR/m3 | 0.12 EUR/kg
| Lifetime |  | 20 years | 20 years | 15 years | 20 years | 30 years
| Fuel cost |  | Green Electricity
Emission reduction rate (?)
Carbon cost
|  | time constant | 10s
|  | efficiency | 0.6-0.78 | COP 4-7 | 99
|  |  | 34.6154 | 23.6258 | 4.8081
0.0046111
(((CAP+ O&M)/(LT))+Carbon penalty)/efficiency cost [EUR/kW]
0.0173
|  |  | wind electrolysis | 16.6 | g CO2/kWh | 1 | EUR/g CO2
|  |  | solar electrolysis | 42.4 | g CO2/kWh | 1 | EUR/g CO2
|  |  | Heat Pump | 62.28 | g CO2/kwh
61.92
[5 empty] | €€€ | 0.0044611
0.0046111
0.0173
|  |  | total greenhouse gas emission of the pathway |  |  |  |  | e
The penalty cost due to CO2 emission (Cenv) of the heat pump system can be calculated as follows:

## Storage
P2G |  |  |  | P2H
molar mass | 2.016*10-3 |  |  | mass flow
specific heat
density | 0.06953 | at 30 bar | at 80 C | density
| 20.2742 | at 350 bar | at 80C