## HP Calculations
Tevaporation
|  | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44 | at 70 celcius
| H1 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 |  |  |  | P2=P3 | 2.1168 | MPa
| H2 | 386.55 | 389.02 | 391.46 | 393.87 | 396.25 | 398.6 | 400.92 | 403.2 | 405.43 | 407.61 | 409.75 | 411.82 | 413.84 | 415.78 | 417.65 | 419.43 | 421.11 | H4 | 428.65 | kj/kg
| S2=S1 | 1.7413 | 1.7379 | 1.7348 | 1.732 | 1.7294 | 1.7271 | 1.725 | 1.723 | 1.7212 | 1.7196 | 1.718 | 1.7166 | 1.7152 | 1.7138 | 1.7124 | 1.7111 | 1.7096 | H5 | 304.28
| H3 | 443.4243 | 442.2412 | 441.1626 | 440.1883 | 439.2836 | 438.4833 | 437.7526 | 437.0566 | 436.4303 | 435.8736 | 435.3168 | 434.8297 | 434.3426 | 433.8554 |  |  |  | S4 | 1.6956 | kj/kg.K
[19 empty] | S5 | 1.3332
|  | pressure | 2 | [6 empty] | Pressure | 2.2 | [6 empty] | pressure | 2.1168
|  | Temp | H | S | [5 empty] | Temp | H | S | [5 empty] | Temp3 | H3
|  | 67.49 | 428.52 | 1.6983 | [5 empty] | 71.74 | 429.08 | 1.6948
|  | 70 | 432.22 | 1.7091
|  | 80 | 445.86 | 1.7483 | [5 empty] | 80 | 441.49 | 1.7303
|  | 90 | 458.49 | 1.7835 | [5 empty] | 90 | 454.98 | 1.768
|  | 100 | [7 empty] | 100 | 467.61 | 1.8023
Linear interpolatation
Same enthalpy
H
|  | 443.4243 | 442.2412 | 441.1626 | 440.1883 | 439.2836 | 438.4833 | 437.7526 | 437.0566 | 436.4303 | 435.8736 | 435.3168 | 434.8297 | 434.3426 | 433.8554
W (kj/kg) | H3-H2 | 56.8743 | 53.2212 | 49.7026 | 46.3183 | 43.0336 | 39.8833 | 36.8326 | 33.8566 | 31.0003 | 28.2636 | 25.5668 | 23.0097 | 20.5026 | 18.0754
Q(kj/kg) | H3-H5 | 139.1443 | 137.9612 | 136.8826 | 135.9083 | 135.0036 | 134.2033 | 133.4726 | 132.7766 | 132.1503 | 131.5936 | 131.0368 | 130.5497 | 130.0626 | 129.5754
COP | Q/W | 2.4465 | 2.5922 | 2.754 | 2.9342 | 3.1372 | 3.3649 | 3.6238 | 3.9217 | 4.2629 | 4.6559 | 5.1253 | 5.6737 | 6.3437 | 7.1686
cycle efficiency | COP(Tcon-Teva)/Teva | 0.86979 | 0.86693 | 0.86476 | 0.86317 | 0.86253 | 0.86232 | 0.86296 | 0.86483 | 0.86708 | 0.86952 | 0.87417 | 0.87831 | 0.88473 | 0.8927
m(kg/s) | 50000(kW)/(Q) | 359.3392 | 362.4207 | 365.2767 | 367.8952 | 370.3606 | 372.5692 | 374.6089 | 376.5723 | 378.3571 | 379.9578 | 381.5721 | 382.9959 | 384.4304 | 385.8757

## p-H cycle table
1
2
3
4
5

## photo
1
2
3
4
5

## COP vs. Teva
Teva | -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32
COP | 2.4465 | 2.5922 | 2.754 | 2.9342 | 3.1372 | 3.3649 | 3.6238 | 3.9217 | 4.2629 | 4.6559 | 5.1253 | 5.6737 | 6.3437 | 7.1686
4th order polynomial function
Linear model Poly4: f(x) = p1*x^4 + p2*x^3 + p3*x^2 + p4*x + p5 Coefficients (with 95% confidence bounds): p1 = 4.539e-07 (3.642e-07, 5.435e-07) p2 = 1.522e-05 (1.275e-05, 1.769e-05) p3 = 0.0008562 (0.000808, 0.0009044) p4 = 0.06064 (0.05981, 0.06146) p5 = 3.37 (3.364, 3.377)
| x | y
| -20 | 2.4465
| -16 | 2.5922
| -12 | 2.754
| -8 | 2.9342
| -4 | 3.1372
| 0 | 3.3649
| 4 | 3.6238
| 8 | 3.9217
| 12 | 4.2629
| 16 | 4.6559
| 20 | 5.1253
| 24 | 5.6737
| 28 | 6.3437
| 32 | 7.1686
36
40

## P2H Models
Modelling Considerations of P2H
Model | Modelling Approach | Dynamic Behaviour | Modelling Scale | COP
A | Regression | Linear | HP | Constant
B | Regression | Non-linear | HP | Variable
C | Regression | Non-linear | HP with auxiliary boiler | Constant

## Boiler
Q | m*c*∆T(40-Twaste)
η | efficiency | 0.99
W | Q/η
m | mass/massflow R134a | 390 | kg/s
c | specific heat capacity | 1.3215 | kJ/(kg.K) | at 40 celcius quality=0.5
Tevaporation
| -20 | -16 | -12 | -8 | -4 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 44
H1 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28 | 304.28
H2 | 386.55 | 389.02 | 391.46 | 393.87 | 396.25 | 398.6 | 400.92 | 403.2 | 405.43 | 407.61 | 409.75 | 411.82 | 413.84 | 415.78 | 417.65 | 419.43 | 421.11
H2-H1 | 82.27 | 84.74 | 87.18 | 89.59 | 91.97 | 94.32 | 96.64 | 98.92 | 101.15 | 103.33 | 105.47 | 107.54 | 109.56 | 111.5 | 113.37 | 115.15 | 116.83
|  | Tamb | Q
|  | -20 | 82.27
|  | -16 | 84.74
|  | -12 | 87.18
|  | -8 | 89.59
|  | -4 | 91.97
|  | 0 | 94.32
|  | 4 | 96.64
|  | 8 | 98.92
|  | 12 | 101.15
|  | 16 | 103.33
|  | 20 | 105.47
|  | 24 | 107.54
|  | 28 | 109.56
|  | 32 | 111.5
|  | 36 | 113.37
|  | 40 | 115.15
|  | 44 | 116.83

## Tamb
Weather archive in Hoek Van Holland weather station number :06330 https://rp5.ru/Weather_archive_in_Hoek_Van_Holland
Ambient Air temperature at 2m
Hour\Day | 2019-02-07 |  | 2019-03-23 |  | 2019-05-07 |  | 2019-06-23 |  | 2019-08-07 |  | 2019-09-23 |  | 2019-11-07 |  | 2019-12-23
| Tamb (⁰C) | DHW Demand (kj/s) | Tamb (⁰C) | DHW Demand (m3/kj) | Tamb (⁰C) | DHW Demand (m3/kj) | Tamb (⁰C) | DHW Demand (m3/kj) | Tamb (⁰C) | DHW Demand (m3/kj) | Tamb (⁰C) | DHW Demand (m3/kj) | Tamb (⁰C) | DHW Demand (m3/kj) | Tamb (⁰C) | DHW Demand (m3/kj)
0:00 | 6.8 |  | 8.6 |  | 5.3 |  | 16.6 |  | 18.6 |  | 16.1 |  | 7.1 |  | 8.6
1:00 | 6.9 |  | 8.8 |  | 5.5 |  | 17 |  | 18.7 |  | 16 |  | 6.8 |  | 8.7
2:00 | 7.3 |  | 8.8 |  | 5 |  | 16.6 |  | 18.4 |  | 15.9 |  | 6.1 |  | 8.9
3:00 | 7.8 |  | 8.7 |  | 5.1 |  | 16 |  | 18.5 |  | 15.9 |  | 6.2 |  | 8.7
4:00 | 8.1 |  | 8.7 |  | 4.9 |  | 15.5 |  | 18.3 |  | 15.8 |  | 6.1 |  | 8.4
5:00 | 8.8 |  | 9 |  | 4.9 |  | 15 |  | 18 |  | 15.7 |  | 7.2 |  | 8.2
6:00 | 9 |  | 9.2 |  | 5.3 |  | 14.9 |  | 18 |  | 15.8 |  | 7.6 |  | 8.4
7:00 | 7.4 |  | 9.1 |  | 6.1 |  | 16.3 |  | 17.2 |  | 15.7 |  | 8 |  | 7.5
8:00 | 6.8 |  | 9.3 |  | 8 |  | 17.8 |  | 18.1 |  | 15.7 |  | 7.7 |  | 7.4
9:00 | 6.7 |  | 9.4 |  | 9.3 |  | 19.9 |  | 18.7 |  | 15.7 |  | 8.3 |  | 8.3
10:00 | 7.1 |  | 9.3 |  | 11.5 |  | 22.2 |  | 19.2 |  | 16 |  | 8.7 |  | 8.1
11:00 | 7.8 |  | 9.4 |  | 10.3 |  | 24.4 |  | 20.1 |  | 16.1 |  | 8.7 |  | 8.3
12:00 | 8.1 |  | 9.1 |  | 12.5 |  | 23.3 |  | 20.4 |  | 17.7 |  | 8.7 |  | 8.5
13:00 | 8.6 |  | 9.7 |  | 13.5 |  | 22.8 |  | 17.7 |  | 16.8 |  | 8.3 |  | 8.8
14:00 | 8.6 |  | 9.9 |  | 12.7 |  | 24.2 |  | 20.1 |  | 17.9 |  | 8.4 |  | 8.8
15:00 | 8.2 |  | 9.9 |  | 14 |  | 24 |  | 21.7 |  | 19.1 |  | 8.1 |  | 8.9
16:00 | 7.8 |  | 9.4 |  | 14.6 |  | 28.2 |  | 21.8 |  | 19.1 |  | 8.3 |  | 8.4
17:00 | 7.2 |  | 9.2 |  | 14.4 |  | 28.7 |  | 21.9 |  | 18.4 |  | 8.8 |  | 8.4
18:00 | 7 |  | 8.2 |  | 14.6 |  | 28.6 |  | 21.5 |  | 18.6 |  | 9.2 |  | 8.2
19:00 | 6.9 |  | 7.2 |  | 14.1 |  | 27.8 |  | 20.8 |  | 17.5 |  | 7.9 |  | 8.1
20:00 | 6.7 |  | 6.9 |  | 13.5 |  | 27.2 |  | 19.8 |  | 15.6 |  | 7.4 |  | 8.5
21:00 | 6.5 |  | 6.5 |  | 12.2 |  | 26.4 |  | 19 |  | 15 |  | 7.2 |  | 9
22:00 | 6.4 |  | 5.8 |  | 11.2 |  | 24.9 |  | 19 |  | 13.8 |  | 6.9 |  | 8.6
23:00 | 6.3 |  | 5.1 |  | 11.1 |  | 24.2 |  | 18.9 |  | 15.8 |  | 6.5 |  | 8
Average | 7.45 | 0 | 8.55 | 0 | 9.9833 | 0 | 21.7708 | 0 | 19.35 | 0 | 16.4875 | 0 | 7.675 | 0 | 8.4042 | 0

## Demand
| TR | Tmin | Q0 | Qmax
gas | 25 | 5 | 0.8(pu) | 1
heat | 25 | 5 | 0.6(pu) | 1
Q(t) = Q0+((Qmax-Q0)/(TR-Tmin))* max(0,TR-T(t))

## Flexibility Deployment
Price Signals for PP
Variables
|  | Efficiency (η) | LC of Energy
| P2G | input from model | Levelized Cost of Hydrogen Production
| P2H | input from model | Levelized Cost of Heat Production
|  |  | Electrolyser | HP
Capital costs (CAPEX)
Operation & maintenance costs
Lifetime
| Fuel cost |  | Both electricity
Emission reduction rate (?)