## Slide 1: Multi Energy Systems: Investigating Hidden Flexibilities Provided by Power-to-X Considering Grid Support Strategies
MSc: Bekir Caner Yagci (4857089)
PhD: Digvijay Gusain
Supervisor: Asst. Prof. Milos Cvetkovic
Delft University of Technology
Faculty of Electrical Engineering,
Mathematics, and Computer Science

## Slide 2: Content
Introduction
    Research Problem
    Flexibility
    Research Questions
Methodology
    Multi-Energy System Design
    Energy Demand Profiles
Modelling & Case Study
    PEM Electrolyser
    Electric Heat Pump
    Power-to-X Models
    Case Study
    Adjustable Power Level Controller
    Co-simulation Setup
Results
Conclusion

## Slide 3: Introduction - Research Problem
Variable nature of renewable energy sources introduces a great challenge for grid operator to balance the electricity supply and demand
Replacing production based on fossil fuels in industries, such as chemicals, petrochemicals, food, steel cement; leads to more sustainable and flexible multi-energy systems
Due to approximations made in model formulations (constant / linear relation between power input and energy output), flexibilities provided by PtX to network can be concealed in the simulation results
Correct efficiency characterization of PtX is crucial to analyze flexibility of power system. Inaccurate efficiency models of PtX may lead to increased transmission losses, higher operational cost or misinterpretation of MES capacity
Existing energy management models for MES do not consider energy cost of production (€/MWh). This results with unnecessary trading of electricity and increase in operational cost
MES: Multi Energy System
PtX: Power-to-X

## Slide 4
” Flexibility is the ability of a component or a collection of components to respond to power fluctuations in power systems. ”
In this project, PtX devices and the flexibility offered by them to support power system is analyzed.
PtX technology offers;
  Larger power balance flexibility
  for the grid
  Opportunities for demand flexibility
  by storage elements
Additional information obtained from detailed models during flexibility analysis is defined as the hidden flexibility of PtX
Introduction - Flexibility
PtX: Power-to-X
An exemplary flexible load measure with the corresponding parameters [1]

## Slide 5: Introduction - Research Questions
Which technologies have the highest potential to provide flexibility?
  Which options are available in industrial area?
  What are the options in order to increase flexibility of an industrial grid?
To what extent does model fidelity impact flexibility analysis?
  Which assumptions can be made and which physical effects should be considered?
How to manage optimal deployment of flexibility considering individual resource constraints?
  How to combine models representing different energy vectors efficiently?
  How complex simulations can be created for energy management of MES?
MES: Multi Energy System
Co-simulation Approach

## Slide 6: Methodolgy – MES Design
PEM: Proton Exchange Membrane
PtG: Power-to-Gas
PtH: Power-to-Heat
RES: Renewable Energy Sources
PEM Electrolyser is one of the most convenient options as a result of hydrogen characteristics.
Electric heat pumps with auxiliary boilers are commonly recommended for their high efficiencies (Bode & Schmitz, 2018).
The hourly power output of RES is calculated from Renewables.ninja [2]

## Slide 7: Methodolgy – Energy Demand Profiles
 | TR [⁰C] | Tmin [⁰C] | Q0 [m3/s] | Qmax [m3/s]
Industrial PtG | 25 | 5 | 3.14e-03 | 3.85e-03
District Heating PtH | 25 | 5 | 3 | 4
Historical ambient temperature data is used for the calculation of energy demand profiles
PtG: Power-to-Gas
PtH: Power-to-Heat
Mathematical formulation of Felten,
Baginski, and Weber (2017) model:
The relation between ambient temperature and hydrogen & heat demand [1]

## Slide 8: Modelling – PEM Electrolyser
Model | Physical Domains | Modelling Approach | Dynamic Behaviour | Modelling Scale
A | Electrochemical Electrical | Analytic + Empirical | Static | Cell/Stack
B | Electrochemical Electrical Thermal | Analytic + Empirical | Static + Dynamic (ODE) | Cell/Stack + BOP
MES: Multi Energy System
ODE: Ordinary Differential Equation
BOP: Balance of Plant
Temperature dependency of electrolyser efficiency is considered
Electrolyser performance is calculated considering operational conditions (temperature, pressure, cell current effects)
Balance of plant elements are considered for temperature evolution

## Slide 9: Modelling – PEM Electrolyser
Thermal submodel
  BOP: circulation pump, cooling system
  Static vs. First order dynamics
Electrochemical:
Pressure:
Massflow:
Thermal:
BOP: Balance of Plant
Model A
Model B

## Slide 10: Modelling – Electric Heat Pump
Model | Modelling Approach | Ambient Temperature | Modelling Scale
A | Regression | Daily Average | Heat Pump
B | Regression | Hourly Measured | Heat Pump
C | Regression | Hourly Measured | Heat Pump with Auxiliary E-Boiler
Model C:
Model B & C:
Model A:

## Slide 11: Modelling – Electric Heat Pump
COP results for various ambient and condenser temperatures:
Figure: Theoretical Single-Stage Vapor Compression Refrigeration Cycle (C:Constant )
Pressure – Enthalpy table of refrigerant R-134a is used for enthalpy calculations with the assumptions shown in the figure

## Slide 12: Modelling – Electric Heat Pump
5th order polynomial fuction parameters for Tcondenser = 50,70 ⁰C
COP curve fitting result for Tcond = 50 ⁰C
COP curve fitting result for Tcond = 70 ⁰C

## Slide 13: Modelling - Power-to-X Models
Electrolyser & Heat Pump, calculate energy output based on power input and operating conditions
Controller, calculates Pmin, Pmax constraints for PandaPower
Storage, calculates amount of stored energy in m3
StaticGenerator, provides electrical interface and controls Qload
Power-to-Gas
Power-to-Heat

## Slide 14: Case Study
Multi-Energy System Analysis:
  It is carried out in order to investigate the seasonal weather behaviour in the area and flexible capacity of MES.
Power-to-X Analysis:
  Efficiency characters of different models compared in order to investigate the effect of temperature evolution on device performance.
Power System Analysis:
  Base case: It is assumed that none of the PtX is available for flexibility service. Without any flexibility service, measuring the flexible demand of MES.
  First case: It is assumed that only one PtXs are available for flexibility service. Comparing both PtX options with respect to reduction in flexible demand of MES after flexibility service. Comparing the energy output of PtX model A, B, C for the same flexibility service.
  Second case: It is assumed that both PtXs are available for flexibility service. Considering cost signals and adjustable power level constraints, measuring the deployment of flexibility between PtG & PtH and quantifying the reduction in total operational cost.
MES: Multi Energy System
PtG: Power-to-Gas
PtH: Power-to-Heat

## Slide 15: Co-Simulation - Optimum Deployment of Flexibility with Hierarchical Energy Management
Objective function:
Cost function:
Constraints:
Element | Constraint | Remark
Power-to-X |  | Operational power constraints (Device flexibility)
Transformer |  | Branch constraint (Maximum loading percentage)
Line |  | Branch constraint (Maximum loading percentage)
Bus |  | Network constraint
Element | Constraint | Remark
Power-to-X |  | Operational power constraints (Device flexibility)
Transformer |  | Branch constraint (Maximum loading percentage)
Line |  | Branch constraint (Maximum loading percentage)
Bus |  | Network constraint

## Slide 16: Modelling – Adjustable Power Level Controller
Constraint decision making:

## Slide 17: Co-Simulation - Levelized Cost of Energy
Calculates

## Slide 18: Co-simulation Flow Chart
MES: Multi Energy System
CEMS: Community Energy Management System
OPF: Optimal Power Flow
Notes: The figure includes the
processes that allow for the storage and transport of electrical energy (Gray blocks)

## Slide 19: Simulation Tools
OpenModelica
    For fast simulation of complex dynamics from different energy domains, using object-oriented programming language
    To export FMU’s for co-simulation
Pandapower
    Optimal power flow solver
    Used for the energy management of MES for various co-simulation cases
Energysim (Co-simulation)
    Allows to implement complex simulations with reduced computational burden by exchanging only necessary variables.
I/O: Input/Output
FMU: Functional Mock-up Unit
OPF: Optimal Power Flow
Co-simulation step and exchange times

## Slide 20: Results - MES Analysis

## Slide 21: Results – PtX Analysis
Max ∆T = 13
Max ∆COPAB = 1.4
Max ∆COPBC = 3
Max ∆η = 0.6%
Max ∆T = 7

## Slide 22: Results – PtX Analysis
Max ∆P = 0.4 MW
Max ∆PAB = 1.4 MW
Max ∆PBC = 5 MW

## Slide 23: Results – Power System Analysis, Case 1
Max ∆Pbase-pth = 10 MW
Max ∆Pbase-ptg = 2 MW
Max ∆H2 = 0.032 m3/s
Max ∆QA-B = 0.20 m3/s
Max ∆QB-C = 0.96 m3/s

## Slide 24: Results – Power System Analysis, Case 2
From 10:00 to 16:00, optimal deployment of flexibility is able to save 2.75€ with respect to 100% PtG priority and 0.99€ with respect to 50% equal priority.

## Slide 25: Conclusion
Detailed thermal models are necessary to accurately represent the efficiency of PtX otherwise flexibility analysis may result with defective outcomes on active power consumption or energy production of PtX.
Optimal deployment of flexibility is able to provide operational cost savings for MES. Multi-layer structure of agent-based hierarchical control enables the implementation of local control objectives for the agents individually and a global objective for MES.
The relevance of co-simulation and Energysim for flexibility analysis of multi-energy systems is clearly supported by the current methodology.
MES: Multi Energy System
PtX: Power-to-X

## Slide 26: References
[1] Jens Weibezahn. Data Documentation 92: Electricity, Heat, and Gas Sector Data for Modeling the Ger- man System.DIW Berlin, 2017, (ISSN 1861-1532), 2017.
[2] Stefan Pfenninger and Iain Staffell. URL http://www.renewables.ninja/.
[3] B. Felten, J. P. Baginski, and C. Weber, “KWK-Mindest- und Maximaleinspeisung - Die Erzeu- gung von Zeitreihen für die Energiesystemmodellierung,” no. 10, 2017.
[4] A. Bloess, W. P. Schill, and A. Zerrahn, “Power-to-heat for renewable energy integration: A review of technologies, modeling approaches, and flexibility potentials,” Appl. Energy, vol. 212, no. August 2017, pp. 1611–1626, 2018.
[5] J. Webster and C. Bode, “Implementation of a Non-Discretized Multiphysics PEM Electrolyzer Model in Modelica,” Proc. 13th Int. Model. Conf. Regensburg, Ger. March 4–6, 2019, vol. 157, pp. 833–840, 2019.
[6] C. Bode and G. Schmitz, “Dynamic simulation and comparison of different configurations for a coupled energy system with 100% renewables,” Energy Procedia, vol. 155, pp. 412–430, 2018.

## Slide 27: Multi Energy Systems: Investigating Hidden Flexibilities Provided by Power-to-X Considering Grid Support Strategies
MSc: Bekir Caner Yagci (4857089)
PhD: Digvijay Gusain
Supervisor: Asst. Prof. Milos Cvetkovic
E-mail: B.C.Yagci@student.tudelft.nl
Version Control: https://github.com/caneryagci/Multi-Energy-Systems-Thesis-Project.git